{"text_format":"1","workbook":"xlsx","n_sheets":11,"sheets":["流出係数算出","降雨強度","流入量定義","01流出計算（Q-Tグラフ）","浸透施設能力","浸透施設能力（貯留浸透モデル_道路管理者用）","02流出計算（QT-Sグラフ）","03-①調整池容量の概算","04-①調節計算（自然調節方式）","04-②調節計算（2段）","04-③調節計算（ポンプ）"],"not_rendered":{"charts":5,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"流出係数算出","index":0,"n_rows":31,"n_cols":10,"rows_kept":31,"cut":false,"hidden":false,"merged":[[7,1,7,4],[26,1,30,3],[1,4,2,5],[23,2,25,3],[18,1,25,1],[8,1,17,1],[4,1,4,7],[18,2,19,3],[8,2,17,3],[6,1,6,3],[20,2,22,3]]}
[null,null,null,null,null,null,null,null,"行為前Σan","行為後Σan"]
[null,null,null,null,"流出係数算定結果",null,"行為前","行為後",{"$f":"SUM($G$9:$G$95)","v":0.26500000000000001},{"$f":"SUM($H$9:$H$95)","v":0.26500000000000001}]
[null,null,null,null,null,null,{"$f":"$I$4/$I$2","v":0.29245283018867929},{"$f":"$J$4/$J$2","v":0.88113207547169803},"行為前Σ(fn*an)","行為後Σ(fn*an)"]
[null,null,null,null,null,null,null,null,{"$f":"SUM($I$9:$I$95)","v":7.7500000000000013E-2},{"$f":"SUM($J$9:$J$95)","v":0.23349999999999999}]
[null,"雨水浸透阻害行為の技術基準として設定する流出係数"]
[]
[null,"区分",null,null,"土地利用の形態の細区分","流出係数","行為前面積\n（ha）","行為後面積\n（ha）"]
[null,"計",null,null,null,"－",{"$f":"SUM(G9:G31)","v":0.26500000000000001},{"$f":"SUM(H9:H31)","v":0.26500000000000001}]
[null,"宅地等に該当する土地","第１号関連",null,"宅地",0.9,0.03,0.12,{"$f":"$F9*$G9","v":2.7E-2},{"$f":"$F9*$H9","v":0.108}]
[null,null,null,null,"池沼",1,null,null,0,0]
[null,null,null,null,"水路",1,null,null,0,0]
[null,null,null,null,"ため池",1,null,null,0,0]
[null,null,null,null,"道路(法面を有しないもの）",0.9,5.0000000000000001E-3,5.0000000000000001E-3,4.5000000000000005E-3,4.5000000000000005E-3]
[null,null,null,null,"道路（法面を有するもの）",null,null,null,0,0]
[null,null,null,null,"鉄道線路（法面を有しないもの）",0.9,null,null,0,0]
[null,null,null,null,"鉄道線路（法面を有するもの）",null,null,null,0,0]
[null,null,null,null,"飛行場（法面を有しないもの）",0.9,null,null,0,0]
[null,null,null,null,"飛行場（法面を有するもの）",null,null,null,0,0]
[null,"宅地等以外の土地","第２号\n関　連",null,"不浸透性材料により舗装された土地（法面を除く）",0.95,null,0.06,0,5.6999999999999995E-2]
[null,null,null,null,"不浸透性材料により覆われた法面",1,null,null,0,0]
[null,null,"第３号\n関　連",null,"ゴルフ場（雨水を排除するための排水施設を伴うものに限る）",0.5,null,null,0,0]
[null,null,null,null,"運動場その他これに類する施設（雨水を排除するための排水施設を伴うものに限る）",0.8,null,0.08,0,6.4000000000000001E-2]
[null,null,null,null,"ローラーその他これに類する建設機械を用いて締め固められた土地",0.5,null,null,0,0]
[null,null,"上記第１号から第３号に掲げる土地以外の土地",null,"山地",0.3,null,null,0,0]
[null,null,null,null,"人工的に造成され植生に覆われた法面",0.4,null,null,0,0]
[null,null,null,null,"林地、耕地、原野その他ローラーその他これに類する建設機械を用いて締め固められていない土地",0.2,0.23,null,{"$f":"$F26*$G26","v":4.6000000000000006E-2},0]
[null,"そ\n\n\nの\n\n\n他",null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,0,0]
[null,null,null,null,null,null,null,null,0,0]

{"sheet":"降雨強度","index":1,"n_rows":38,"n_cols":12,"rows_kept":38,"cut":false,"hidden":false,"merged":[]}
["※降雨は対象地域の降雨に変更して下さい"]
["時","分","降雨量\n（mm/h）","時","分","降雨量\n（mm/h）","時","分","降雨量\n（mm/h）","時","分","降雨量\n（mm/h）"]
[0,"0－10",3.3208415013855985,6,"0－10",5.9693440612808448,12,"0－10",75.621841256970711,18,"0－10",5.7641058705103436]
[null,"10－20",3.3597993966681319,null,"10－20",6.1154031222507914,null,"10－20",50.160598521771021,null,"10－20",5.6357024802028493]
[null,"20－30",3.3998016020827437,null,"20－30",6.2695815901108753,null,"20－30",40.319414784519012,null,"20－30",5.5134595053787736]
[null,"30－40",3.440891931015722,null,"30－40",6.4325903073559632,null,"30－40",34.692527456442058,null,"30－40",5.3969356886937483]
[null,"40－50",3.4831167104453247,null,"40－50",6.6052261660887783,null,"40－50",30.929187738484782,null,"40－50",5.2857311892217469]
[null,"50－60",3.5265249647946577,null,"50－60",6.7883855727023734,null,"50－60",28.183572273256257,null,"50－60",5.1794828224445162]
[1,"0－10",3.5711686161983383,7,"0－10",6.9830805262165088,13,"0－10",26.065741839804573,19,"0－10",5.0778599427750128]
[null,"10－20",3.6171027029429754,null,"10－20",7.1904579225062442,null,"10－20",24.367471424486293,null,"10－20",4.9805608695709003]
[null,"20－30",3.6643856180105789,null,"20－30",7.4118228663613994,null,"20－30",22.966044704653736,null,"20－30",4.8873097747102072]
[null,"30－40",3.7130793699456266,null,"30－40",7.6486669978447486,null,"30－40",17.38718112646302,null,"30－40",4.7978539635784045]
[null,"40－50",3.763249868509388,null,"40－50",7.9027031393130418,null,"40－50",16.068445638619064,null,"40－50",4.7119614926246642]
[null,"50－60",3.8149672379267487,null,"50－60",8.1759079737143452,null,"50－60",14.945542841015994,null,"50－60",4.6294190758148721]
[2,"0－10",3.8683061608836855,8,"0－10",8.4705750157333917,14,"0－10",13.977552048782014,20,"0－10",4.5500302399021173]
[null,"10－20",3.9233462568687405,null,"10－20",8.7893808963401181,null,"10－20",13.134244456342254,null,"10－20",4.4736136946466107]
[null,"20－30",3.9801724989280505,null,"20－30",9.1354690398021496,null,"20－30",12.392798013585741,null,"20－30",4.4000018893078057]
[null,"30－40",4.0388756734572331,null,"30－40",9.5125563075499837,null,"30－40",11.735655567399204,null,"30－40",4.3290397310048778]
[null,"40－50",4.0995528883467394,null,"40－50",9.9250703258388739,null,"40－50",11.14908679440614,null,"40－50",4.2605834441368415]
[null,"50－60",4.1623081354828404,null,"50－60",10.378328331019624,null,"50－60",10.62219774771296,null,"50－60",4.194499553085393]
[3,"0－10",4.2272529145588358,9,"0－10",10.878772977240363,15,"0－10",10.146233280195919,21,"0－10",4.130663972880189]
[null,"10－20",4.2945069261222448,null,"10－20",11.434287498047981,null,"10－20",9.7140759353999453,null,"10－20",4.0689611947012283]
[null,"20－30",4.3641988430155614,null,"20－30",12.054623291842383,null,"20－30",9.3198795763826077,null,"20－30",4.0092835548608043]
[null,"30－40",4.436467170765491,null,"30－40",12.751989785417017,null,"30－40",8.9587972583159186,null,"30－40",3.9515305774453968]
[null,"40－50",4.511461209126856,null,"40－50",13.541883473181224,null,"40－50",8.6267761991269722,null,"40－50",3.8956083820724876]
[null,"50－60",4.5893421289752041,null,"50－60",14.444277829446129,null,"50－60",8.3204012925612005,null,"50－60",3.8414291493847488]
[4,"0－10",4.6702841810061955,10,"0－10",15.485372370019061,16,"0－10",8.0367742541038414,22,"0－10",3.7889106377862394]
[null,"10－20",4.7544760554992997,null,"10－20",16.700234800177171,null,"10－20",7.7734192729464109,null,"10－20",3.7379757457833422]
[null,"20－30",4.8421224156640621,null,"20－30",18.136920598395207,null,"20－30",7.5282086222926869,null,"20－30",3.6885521149712535]
[null,"30－40",4.9334456310139334,null,"30－40",23.635273992650959,null,"30－40",7.2993034668824981,null,"30－40",3.6405717693605997]
[null,"40－50",5.0286877419052196,null,"40－50",25.173211892113866,null,"40－50",7.0851063626301318,null,"40－50",3.5939707871582187]
[null,"50－60",5.1281126920782754,null,"50－60",27.061916288284138,null,"50－60",6.8842228381840194,null,"50－60",3.5486890016973804]
[5,"0－10",5.232008872907091,11,"0－10",29.459601612195971,17,"0－10",6.6954300939407636,23,"0－10",3.5046697285028587]
[null,"10－20",5.3406920313470891,null,"10－20",32.64706921855899,null,"10－20",6.5176513253210722,null,"10－20",3.4618595158782002]
[null,"20－30",5.4545086038368034,null,"20－30",37.185686195049911,null,"20－30",6.3499345249179449,null,"20－30",3.4202079166658907]
[null,"30－40",5.5738395508055421,null,"30－40",44.42836096834376,null,"30－40",6.1914348772581436,null,"30－40",3.3796672791352651]
[null,"40－50",5.6991047818120482,null,"40－50",59.003824273087865,null,"40－50",6.041400054925294,null,"40－50",3.3401925551253275]
[null,"50－60",5.8307682803960468,null,"50－60",148.09736170378781,null,"50－60",5.8991578728134302,null,"50－60",3.3017411238062553]

{"sheet":"流入量定義","index":2,"n_rows":147,"n_cols":2,"rows_kept":147,"cut":false,"hidden":false,"merged":[]}
["※流出計算を実行する場合、記入する必要はありません。"]
["時刻","行為後流入量"]
["00:00:00"]
["00:10:00",0]
["00:20:00",6.9999999999999999E-4]
["00:30:00",7.2000000000000005E-4]
["00:40:00",7.2000000000000005E-4]
["00:50:00",7.2000000000000005E-4]
["01:00:00",7.5000000000000002E-4]
["01:10:00",7.5000000000000002E-4]
["01:20:00",7.5000000000000002E-4]
["01:30:00",7.7999999999999999E-4]
["01:40:00",7.7999999999999999E-4]
["01:50:00",7.7999999999999999E-4]
["02:00:00",8.0000000000000004E-4]
["02:10:00",8.0000000000000004E-4]
["02:20:00",8.1999999999999998E-4]
["02:30:00",8.1999999999999998E-4]
["02:40:00",8.1999999999999998E-4]
["02:50:00",8.4999999999999995E-4]
["03:00:00",8.4999999999999995E-4]
["03:10:00",8.8000000000000003E-4]
["03:20:00",8.8000000000000003E-4]
["03:30:00",8.9999999999999998E-4]
["03:40:00",8.9999999999999998E-4]
["03:50:00",9.3000000000000005E-4]
["04:00:00",9.3000000000000005E-4]
["04:10:00",9.5E-4]
["04:20:00",9.7000000000000005E-4]
["04:30:00",9.7000000000000005E-4]
["04:40:00",1E-3]
["04:50:00",1E-3]
["05:00:00",1.0200000000000001E-3]
["05:10:00",1.0499999999999999E-3]
["05:20:00",1.07E-3]
["05:30:00",1.07E-3]
["05:40:00",1.1000000000000001E-3]
["05:50:00",1.1299999999999999E-3]
["06:00:00",1.15E-3]
["06:10:00",1.1800000000000001E-3]
["06:20:00",1.1999999999999999E-3]
["06:30:00",1.23E-3]
["06:40:00",1.25E-3]
["06:50:00",1.2800000000000001E-3]
["07:00:00",1.2999999999999999E-3]
["07:10:00",1.3500000000000001E-3]
["07:20:00",1.3799999999999999E-3]
["07:30:00",1.4E-3]
["07:40:00",1.4499999999999999E-3]
["07:50:00",1.5E-3]
["08:00:00",1.5200000000000001E-3]
["08:10:00",1.58E-3]
["08:20:00",1.6299999999999999E-3]
["08:30:00",1.6800000000000001E-3]
["08:40:00",1.75E-3]
["08:50:00",1.8E-3]
["09:00:00",1.8799999999999999E-3]
["09:10:00",1.9499999999999999E-3]
["09:20:00",2.0500000000000002E-3]
["09:30:00",2.1299999999999999E-3]
["09:40:00",2.2499999999999998E-3]
["09:50:00",2.3500000000000001E-3]
["10:00:00",2.47E-3]
["10:10:00",2.65E-3]
["10:20:00",2.8E-3]
["10:30:00",3.0300000000000001E-3]
["10:40:00",3.2499999999999999E-3]
["10:50:00",3.5500000000000002E-3]
["11:00:00",3.8999999999999998E-3]
["11:10:00",4.3499999999999997E-3]
["11:20:00",4.9500000000000004E-3]
["11:30:00",5.7800000000000004E-3]
["11:40:00",6.9800000000000001E-3]
["11:50:00",8.9800000000000001E-3]
["12:00:00",1.3050000000000001E-2]
["12:10:00",2.9000000000000001E-2]
["12:20:00",1.7399999999999999E-2]
["12:30:00",1.06E-2]
["12:40:00",7.8499999999999993E-3]
["12:50:00",6.3299999999999997E-3]
["13:00:00",5.3299999999999997E-3]
["13:10:00",4.62E-3]
["13:20:00",4.13E-3]
["13:30:00",3.7200000000000002E-3]
["13:40:00",3.3999999999999998E-3]
["13:50:00",3.13E-3]
["14:00:00",2.8999999999999998E-3]
["14:10:00",2.7299999999999998E-3]
["14:20:00",2.5500000000000002E-3]
["14:30:00",2.4299999999999999E-3]
["14:40:00",2.3E-3]
["14:50:00",2.1700000000000001E-3]
["15:00:00",2.0799999999999998E-3]
["15:10:00",2E-3]
["15:20:00",1.92E-3]
["15:30:00",1.8500000000000001E-3]
["15:40:00",1.7700000000000001E-3]
["15:50:00",1.73E-3]
["16:00:00",1.65E-3]
["16:10:00",1.6000000000000001E-3]
["16:20:00",1.5499999999999999E-3]
["16:30:00",1.5E-3]
["16:40:00",1.48E-3]
["16:50:00",1.4300000000000001E-3]
["17:00:00",1.4E-3]
["17:10:00",1.3500000000000001E-3]
["17:20:00",1.32E-3]
["17:30:00",1.2999999999999999E-3]
["17:40:00",1.2800000000000001E-3]
["17:50:00",1.23E-3]
["18:00:00",1.1999999999999999E-3]
["18:10:00",1.1800000000000001E-3]
["18:20:00",1.15E-3]
["18:30:00",1.1299999999999999E-3]
["18:40:00",1.1299999999999999E-3]
["18:50:00",1.1000000000000001E-3]
["19:00:00",1.07E-3]
["19:10:00",1.0499999999999999E-3]
["19:20:00",1.0200000000000001E-3]
["19:30:00",1.0200000000000001E-3]
["19:40:00",1E-3]
["19:50:00",9.7000000000000005E-4]
["20:00:00",9.7000000000000005E-4]
["20:10:00",9.5E-4]
["20:20:00",9.5E-4]
["20:30:00",9.3000000000000005E-4]
["20:40:00",9.3000000000000005E-4]
["20:50:00",8.9999999999999998E-4]
["21:00:00",8.9999999999999998E-4]
["21:10:00",8.8000000000000003E-4]
["21:20:00",8.8000000000000003E-4]
["21:30:00",8.4999999999999995E-4]
["21:40:00",8.4999999999999995E-4]
["21:50:00",8.1999999999999998E-4]
["22:00:00",8.1999999999999998E-4]
["22:10:00",8.0000000000000004E-4]
["22:20:00",8.0000000000000004E-4]
["22:30:00",8.0000000000000004E-4]
["22:40:00",7.7999999999999999E-4]
["22:50:00",7.7999999999999999E-4]
["23:00:00",7.7999999999999999E-4]
["23:10:00",7.5000000000000002E-4]
["23:20:00",7.5000000000000002E-4]
["23:30:00",7.5000000000000002E-4]
["23:40:00",7.2000000000000005E-4]
["23:50:00",7.2000000000000005E-4]
["24:00",0]

{"sheet":"01流出計算（Q-Tグラフ）","index":3,"n_rows":149,"n_cols":11,"rows_kept":149,"cut":false,"hidden":false,"merged":[[1,1,1,5],[1,7,1,24],[22,2,24,4],[9,2,12,4],[17,2,18,5]]}
[]
[null,"流 出 計 算 条 件",null,null,null,null,null,"流 出 計 算 結 果"]
[]
[null,null,null,null,null,null,null,"時刻","行為前流入量","行為後流入量","降雨強度"]
[null,1,"流出計算の実行",null,null,null,null,"00:00:00",0,0]
[null,null,null,null,null,null,null,"00:10:00",7.7999999999999999E-4,2.3500000000000001E-3,3.6227361833297436]
[null,null,"行為面積",{"$f":"流出係数算出!$H$8","v":0.26500000000000001},"ha",null,null,"00:20:00",7.9000000000000001E-4,2.3800000000000002E-3,3.6652357054561433]
[null,null,null,null,null,null,null,"00:30:00",8.0000000000000004E-4,2.4099999999999998E-3,3.7088744749993565]
[null,null,"降雨量",null,null,null,null,"00:40:00",8.0999999999999996E-4,2.4299999999999999E-3,3.7537002883807871]
[null,null,"※「降雨強度」シートに基準降雨を入力してください。（都道府県知事等により公示されている「基準降雨」の値に変更してください。）",null,null,null,null,"00:50:00",8.1999999999999998E-4,2.4599999999999999E-3,3.7997636841221718]
[null,null,null,null,null,null,null,"01:00:00",8.3000000000000001E-4,2.49E-3,3.8471181434123536]
[null,null,null,null,null,null,null,"01:10:00",8.4000000000000003E-4,2.5300000000000001E-3,3.8958203085800047]
[null,null,null,null,null,null,null,"01:20:00",8.4999999999999995E-4,2.5600000000000002E-3,3.9459302213923362]
[null,null,null,null,null,null,null,"01:30:00",8.5999999999999998E-4,2.5899999999999999E-3,3.9975115832842674]
[null,null,"流出係数",null,null,null,null,"01:40:00",8.7000000000000001E-4,2.63E-3,4.050632039940683]
[null,null,"行為前",0.29245283018867929,null,null,null,"01:50:00",8.8000000000000003E-4,2.66E-3,4.1053634929193317]
[null,null,"行為後",0.88113207547169803,null,null,null,"02:00:00",8.8999999999999995E-4,2.7000000000000001E-3,4.1617824413746343]
[null,null,"※「流出係数算出」シートで算出した諸元が入力されていますが、必要に応じて申請図書記載値に上書きすることができます。",null,null,null,null,"02:10:00",9.1E-4,2.7399999999999998E-3,4.2199703573276564]
[null,null,null,null,null,null,null,"02:20:00",9.2000000000000003E-4,2.7799999999999999E-3,4.2800140984022619]
[null,null,null,null,null,null,null,"02:30:00",9.3000000000000005E-4,2.82E-3,4.3420063624669636]
[null,null,"流出計算結果の指定",null,null,null,null,"02:40:00",9.5E-4,2.8600000000000001E-3,4.4060461892260721]
[null,null,null,null,null,null,null,"02:50:00",9.6000000000000002E-4,2.8999999999999998E-3,4.4722395145600782]
[null,null,"※「流入量定義」シートに計算された流出計算結果（行為後）を入力してください。",null,null,null,null,"03:00:00",9.7999999999999997E-4,2.9399999999999999E-3,4.5406997841630981]
[null,null,null,null,null,null,null,"03:10:00",9.8999999999999999E-4,2.99E-3,4.6115486340641834]
[null,null,null,null,null,null,null,"03:20:00",1.01E-3,3.0400000000000002E-3,4.6849166466788121]
[null,null,null,null,null,null,null,"03:30:00",1.0200000000000001E-3,3.0899999999999999E-3,4.7609441923806113]
[null,null,"許容放流量",0.01,"m3/s",null,null,"03:40:00",1.0399999999999999E-3,3.14E-3,4.8397823681078078]
[null,null,null,null,null,null,null,"03:50:00",1.06E-3,3.1900000000000001E-3,4.9215940463202061]
[null,null,null,null,null,null,null,"04:00:00",1.08E-3,3.2499999999999999E-3,5.0065550497911318]
[null,null,null,null,null,null,null,"04:10:00",1.1000000000000001E-3,3.3E-3,5.0948554701885769]
[null,null,null,null,null,null,null,"04:20:00",1.1100000000000001E-3,3.3600000000000001E-3,5.1867011514537804]
[null,null,null,null,null,null,null,"04:30:00",1.14E-3,3.4299999999999999E-3,5.2823153625426125]
[null,null,null,null,null,null,null,"04:40:00",1.16E-3,3.49E-3,5.3819406883788359]
[null,null,null,null,null,null,null,"04:50:00",1.1800000000000001E-3,3.5599999999999998E-3,5.4858411729875112]
[null,null,null,null,null,null,null,"05:00:00",1.1999999999999999E-3,3.63E-3,5.5943047549944822]
[null,null,null,null,null,null,null,"05:10:00",1.23E-3,3.7000000000000002E-3,5.7076460431713709]
[null,null,null,null,null,null,null,"05:20:00",1.25E-3,3.7799999999999999E-3,5.8262094887422791]
[null,null,null,null,null,null,null,"05:30:00",1.2800000000000001E-3,3.8600000000000001E-3,5.9503730223674207]
[null,null,null,null,null,null,null,"05:40:00",1.31E-3,3.9399999999999999E-3,6.0805522372424088]
[null,null,null,null,null,null,null,"05:50:00",1.34E-3,4.0299999999999997E-3,6.2172052165222338]
[null,null,null,null,null,null,null,"06:00:00",1.3699999999999999E-3,4.13E-3,6.3608381240684135]
[null,null,null,null,null,null,null,"06:10:00",1.4E-3,4.2199999999999998E-3,6.5120117032154665]
[null,null,null,null,null,null,null,"06:20:00",1.4300000000000001E-3,4.3299999999999996E-3,6.6713488606372264]
[null,null,null,null,null,null,null,"06:30:00",1.47E-3,4.4400000000000004E-3,6.8395435528482267]
[null,null,null,null,null,null,null,"06:40:00",1.5100000000000001E-3,4.5500000000000002E-3,7.0173712443883227]
[null,null,null,null,null,null,null,"06:50:00",1.5499999999999999E-3,4.6699999999999997E-3,7.2057012720968485]
[null,null,null,null,null,null,null,"07:00:00",1.5900000000000001E-3,4.7999999999999996E-3,7.4055115338571333]
[null,null,null,null,null,null,null,"07:10:00",1.64E-3,4.9399999999999999E-3,7.617906028599827]
[null,null,null,null,null,null,null,"07:20:00",1.6900000000000001E-3,5.0899999999999999E-3,7.8441359154613561]
[null,null,null,null,null,null,null,"07:30:00",1.74E-3,5.2399999999999999E-3,8.0856249451215252]
[null,null,null,null,null,null,null,"07:40:00",1.7899999999999999E-3,5.4099999999999999E-3,8.344000361285179]
[null,null,null,null,null,null,null,"07:50:00",1.8500000000000001E-3,5.5900000000000004E-3,8.6211306974324078]
[null,null,null,null,null,null,null,"08:00:00",1.92E-3,5.7800000000000004E-3,8.9191723349611038]
[null,null,null,null,null,null,null,"08:10:00",1.99E-3,5.9899999999999997E-3,9.2406272898909716]
[null,null,null,null,null,null,null,"08:20:00",2.0600000000000002E-3,6.2199999999999998E-3,9.588415523280128]
[null,null,null,null,null,null,null,"08:30:00",2.14E-3,6.4599999999999996E-3,9.9659662252387076]
[null,null,null,null,null,null,null,"08:40:00",2.2300000000000002E-3,6.7299999999999999E-3,10.377334153690891]
[null,null,null,null,null,null,null,"08:50:00",2.33E-3,7.0200000000000002E-3,10.827349446369681]
[null,null,null,null,null,null,null,"09:00:00",2.4299999999999999E-3,7.3400000000000002E-3,11.321812724748678]
[null,null,null,null,null,null,null,"09:10:00",2.5500000000000002E-3,7.7000000000000002E-3,11.867752338807668]
[null,null,null,null,null,null,null,"09:20:00",2.6800000000000001E-3,8.09E-3,12.473768179688705]
[null,null,null,null,null,null,null,"09:30:00",2.8300000000000001E-3,8.5299999999999994E-3,13.150498136555324]
[null,null,null,null,null,null,null,"09:40:00",2.99E-3,9.0200000000000002E-3,13.911261584091289]
[null,null,null,null,null,null,null,"09:50:00",3.1800000000000001E-3,9.58E-3,14.772963788924971]
[null,null,null,null,null,null,null,"10:00:00",3.3899999999999998E-3,1.022E-2,15.757393995759411]
[null,null,null,null,null,null,null,"10:10:00",3.63E-3,1.0959999999999999E-2,16.893133494566246]
[null,null,null,null,null,null,null,"10:20:00",3.9199999999999999E-3,1.1809999999999999E-2,18.218437963829636]
[null,null,null,null,null,null,null,"10:30:00",4.2500000000000003E-3,1.2829999999999999E-2,19.785731561885676]
[null,null,null,null,null,null,null,"10:40:00",5.5399999999999998E-3,1.6719999999999999E-2,25.783935264710134]
[null,null,null,null,null,null,null,"10:50:00",5.8999999999999999E-3,1.7809999999999999E-2,27.461685700487852]
[null,null,null,null,null,null,null,"11:00:00",6.3499999999999997E-3,1.915E-2,29.522090496309964]
[null,null,null,null,null,null,null,"11:10:00",6.9100000000000003E-3,2.0840000000000001E-2,32.137747213304692]
[null,null,null,null,null,null,null,"11:20:00",7.6600000000000001E-3,2.3099999999999999E-2,35.614984602064347]
[null,null,null,null,null,null,null,"11:30:00",8.7200000000000003E-3,2.631E-2,40.566203121872626]
[null,null,null,null,null,null,null,"11:40:00",1.042E-2,3.143E-2,48.467302874556822]
[null,null,null,null,null,null,null,"11:50:00",1.384E-2,4.1739999999999999E-2,64.367808297914024]
[null,null,null,null,null,null,null,"12:00:00",3.4729999999999997E-2,0.10477,161.56075822231398]
[null,null,null,null,null,null,null,"12:10:00",1.7729999999999999E-2,5.3499999999999999E-2,82.496554098513485]
[null,null,null,null,null,null,null,"12:20:00",1.176E-2,3.5490000000000001E-2,54.720652932841105]
[null,null,null,null,null,null,null,"12:30:00",9.4500000000000001E-3,2.852E-2,43.984816128566194]
[null,null,null,null,null,null,null,"12:40:00",8.1300000000000001E-3,2.4539999999999999E-2,37.846393588845878]
[null,null,null,null,null,null,null,"12:50:00",7.2500000000000004E-3,2.188E-2,33.740932078347029]
[null,null,null,null,null,null,null,"13:00:00",6.6100000000000004E-3,1.9939999999999999E-2,30.745715207188638]
[null,null,null,null,null,null,null,"13:10:00",6.11E-3,1.8440000000000002E-2,28.435354734332257]
[null,null,null,null,null,null,null,"13:20:00",5.7099999999999998E-3,1.7239999999999998E-2,26.582696099439591]
[null,null,null,null,null,null,null,"13:30:00",5.3899999999999998E-3,1.6250000000000001E-2,25.053866950531347]
[null,null,null,null,null,null,null,"13:40:00",4.0800000000000003E-3,1.23E-2,18.967833956141476]
[null,null,null,null,null,null,null,"13:50:00",3.7699999999999999E-3,1.137E-2,17.529213423948068]
[null,null,null,null,null,null,null,"14:00:00",3.5000000000000001E-3,1.057E-2,16.304228553835628]
[null,null,null,null,null,null,null,"14:10:00",3.2799999999999999E-3,9.8899999999999995E-3,15.248238598671286]
[null,null,null,null,null,null,null,"14:20:00",3.0799999999999998E-3,9.2899999999999996E-3,14.328266679646093]
[null,null,null,null,null,null,null,"14:30:00",2.9099999999999998E-3,8.77E-3,13.519416014820807]
[null,null,null,null,null,null,null,"14:40:00",2.7499999999999998E-3,8.3000000000000001E-3,12.802533346253677]
[null,null,null,null,null,null,null,"14:50:00",2.6099999999999999E-3,7.8899999999999994E-3,12.162640139352151]
[null,null,null,null,null,null,null,"15:00:00",2.49E-3,7.5100000000000002E-3,11.587852088414138]
[null,null,null,null,null,null,null,"15:10:00",2.3800000000000002E-3,7.1799999999999998E-3,11.068618123850092]
[null,null,null,null,null,null,null,"15:20:00",2.2799999999999999E-3,6.8700000000000002E-3,10.59717374770903]
[null,null,null,null,null,null,null,"15:30:00",2.1900000000000001E-3,6.5900000000000004E-3,10.167141356053753]
[null,null,null,null,null,null,null,"15:40:00",2.0999999999999999E-3,6.3400000000000001E-3,9.7732333727082725]
[null,null,null,null,null,null,null,"15:50:00",2.0200000000000001E-3,6.1000000000000004E-3,9.4110285808657856]
[null,null,null,null,null,null,null,"16:00:00",1.9499999999999999E-3,5.8900000000000003E-3,9.0768014100667642]
[null,null,null,null,null,null,null,"16:10:00",1.8799999999999999E-3,5.6899999999999997E-3,8.7673900953860073]
[null,null,null,null,null,null,null,"16:20:00",1.82E-3,5.4999999999999997E-3,8.4800937523051747]
[null,null,null,null,null,null,null,"16:30:00",1.7700000000000001E-3,5.3299999999999997E-3,8.2125912243192936]
[null,null,null,null,null,null,null,"16:40:00",1.7099999999999999E-3,5.1599999999999997E-3,7.9628765093263603]
[null,null,null,null,null,null,null,"16:50:00",1.66E-3,5.0099999999999997E-3,7.7292069410510518]
[null,null,null,null,null,null,null,"17:00:00",1.6100000000000001E-3,4.8700000000000002E-3,7.5100612780189291]
[null,null,null,null,null,null,null,"17:10:00",1.57E-3,4.7400000000000003E-3,7.3041055570262863]
[null,null,null,null,null,null,null,"17:20:00",1.5299999999999999E-3,4.6100000000000004E-3,7.1101650821684412]
[null,null,null,null,null,null,null,"17:30:00",1.49E-3,4.4900000000000001E-3,6.9272012999104842]
[null,null,null,null,null,null,null,"17:40:00",1.4499999999999999E-3,4.3800000000000002E-3,6.7542925933725195]
[null,null,null,null,null,null,null,"17:50:00",1.42E-3,4.2700000000000004E-3,6.5906182417366832]
[null,null,null,null,null,null,null,"18:00:00",1.3799999999999999E-3,4.1700000000000001E-3,6.4354449521601049]
[null,null,null,null,null,null,null,"18:10:00",1.3500000000000001E-3,4.0800000000000003E-3,6.2881154951021925]
[null,null,null,null,null,null,null,"18:20:00",1.32E-3,3.9899999999999996E-3,6.1480390693121985]
[null,null,null,null,null,null,null,"18:30:00",1.2899999999999999E-3,3.8999999999999998E-3,6.0146830967768432]
[null,null,null,null,null,null,null,"18:40:00",1.2700000000000001E-3,3.82E-3,5.8875662058477243]
[null,null,null,null,null,null,null,"18:50:00",1.24E-3,3.7399999999999998E-3,5.7662522064237232]
[null,null,null,null,null,null,null,"19:00:00",1.2099999999999999E-3,3.6600000000000001E-3,5.6503448972121983]
[null,null,null,null,null,null,null,"19:10:00",1.1900000000000001E-3,3.5899999999999999E-3,5.5394835739363772]
[null,null,null,null,null,null,null,"19:20:00",1.17E-3,3.5200000000000001E-3,5.4333391304409817]
[null,null,null,null,null,null,null,"19:30:00",1.15E-3,3.46E-3,5.3316106633202249]
[null,null,null,null,null,null,null,"19:40:00",1.1299999999999999E-3,3.3899999999999998E-3,5.2340225057218959]
[null,null,null,null,null,null,null,"19:50:00",1.1000000000000001E-3,3.3300000000000001E-3,5.1403216283178148]
[null,null,null,null,null,null,null,"20:00:00",1.09E-3,3.2799999999999999E-3,5.0502753554344055]
[null,null,null,null,null,null,null,"20:10:00",1.07E-3,3.2200000000000002E-3,4.9636693526204905]
[null,null,null,null,null,null,null,"20:20:00",1.0499999999999999E-3,3.16E-3,4.880305848705393]
[null,null,null,null,null,null,null,"20:30:00",1.0300000000000001E-3,3.1099999999999999E-3,4.8000020610630596]
[null,null,null,null,null,null,null,"20:40:00",1.0200000000000001E-3,3.0599999999999998E-3,4.7225887974598662]
[null,null,null,null,null,null,null,"20:50:00",1E-3,3.0100000000000001E-3,4.6479092117856453]
[null,null,null,null,null,null,null,"21:00:00",9.7999999999999997E-4,2.97E-3,4.5758176942749742]
[null,null,null,null,null,null,null,"21:10:00",9.7000000000000005E-4,2.9199999999999999E-3,4.5061788795056597]
[null,null,null,null,null,null,null,"21:20:00",9.5E-4,2.8800000000000002E-3,4.4388667578558847]
[null,null,null,null,null,null,null,"21:30:00",9.3999999999999997E-4,2.8400000000000001E-3,4.3737638780299672]
[null,null,null,null,null,null,null,"21:40:00",9.3000000000000005E-4,2.8E-3,4.3107606299404324]
[null,null,null,null,null,null,null,"21:50:00",9.1E-4,2.7599999999999999E-3,4.2497545986245315]
[null,null,null,null,null,null,null,"22:00:00",8.9999999999999998E-4,2.7200000000000002E-3,4.1906499811469979]
[null,null,null,null,null,null,null,"22:10:00",8.8999999999999995E-4,2.6800000000000001E-3,4.1333570594031697]
[null,null,null,null,null,null,null,"22:20:00",8.8000000000000003E-4,2.64E-3,4.0777917226727363]
[null,null,null,null,null,null,null,"22:30:00",8.5999999999999998E-4,2.6099999999999999E-3,4.0238750345140941]
[null,null,null,null,null,null,null,"22:40:00",8.4999999999999995E-4,2.5799999999999998E-3,3.9715328393024718]
[null,null,null,null,null,null,null,"22:50:00",8.4000000000000003E-4,2.5400000000000002E-3,3.9206954041726019]
[null,null,null,null,null,null,null,"23:00:00",8.3000000000000001E-4,2.5100000000000001E-3,3.8712970927607784]
[null,null,null,null,null,null,null,"23:10:00",8.1999999999999998E-4,2.48E-3,3.8232760674576638]
[null,null,null,null,null,null,null,"23:20:00",8.0999999999999996E-4,2.4499999999999999E-3,3.7765740173216726]
[null,null,null,null,null,null,null,"23:30:00",8.0000000000000004E-4,2.4199999999999998E-3,3.731135909090062]
[null,null,null,null,null,null,null,"23:40:00",7.9000000000000001E-4,2.3900000000000002E-3,3.6869097590566522]
[null,null,null,null,null,null,null,"23:50:00",7.7999999999999999E-4,2.3600000000000001E-3,3.6438464237730841]
[null,null,null,null,null,null,null,1,7.6999999999999996E-4,2.3400000000000001E-3,3.6018994077886415]

{"sheet":"浸透施設能力","index":4,"n_rows":62,"n_cols":19,"rows_kept":62,"cut":false,"hidden":false,"merged":[[1,1,1,6],[1,12,1,17],[2,2,2,3],[2,6,2,7],[2,13,2,14],[2,17,2,18],[3,2,3,3],[3,13,3,14],[7,1,9,1],[7,2,7,3],[7,4,9,4],[7,5,7,7],[7,12,9,12],[7,13,9,13],[7,14,9,14],[8,2,9,2],[8,3,9,3],[21,1,23,1],[21,2,21,3],[21,4,23,4],[21,5,21,7],[35,1,37,1],[35,2,35,3],[35,4,37,4],[35,5,35,7],[22,2,23,2],[36,2,37,2],[49,13,51,13],[49,14,51,14],[21,13,23,13],[21,14,23,14],[22,3,23,3],[21,12,23,12],[35,14,37,14],[35,13,37,13],[35,12,37,12],[36,3,37,3],[49,1,51,1],[49,2,49,3],[49,4,51,4],[49,5,49,7],[49,12,51,12],[50,2,51,2],[50,3,51,3]]}
[]
[null,"浸透施設能力算定結果",null,null,null,null,null,null,null,null,null,null,"空隙貯留量算定結果"]
[null,"浸透マス","浸透トレンチ",null,"透水性舗装","その他","浸透施設能力算定結果",null,null,null,null,null,"浸透マス","浸透トレンチ",null,"透水性舗装","その他","空隙貯留量算定結果"]
[null,{"$f":"SUM(I11:J20)","v":0},{"$f":"SUM(J25:J34)","v":0},null,{"$f":"SUM(J39:J48)","v":0},{"$f":"SUM(J53:J62)","v":0},{"$f":"B4+C4+E4+F4","v":0},"ｍ3/ｈｒ",null,null,null,null,{"$f":"SUM(K11:K20)/100","v":20},{"$f":"SUM(K25:K34)/100","v":0},null,{"$f":"SUM(K39:K48)/100","v":0},{"$f":"SUM(K53:K62)/100","v":0},{"$f":"M4+N4+P4+Q4","v":20},"ｍ3"]
[null,null,null,null,null,null,{"$f":"G4/3600","v":0},"ｍ3/s"]
[]
[null,"条件設定",null,null,null,null,null,null,null,null,null,null,"条件設定"]
[null,"【浸透マス】","単位設計浸透能（ｍ3/ｈｒ/個）",null,"設置数量\n（個）","影響係数",null,null,null,null,null,null,"【浸透マス】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,"（1）","（2）","（3）"]
[null,null,null,null,null,"内容（１）","内容（２）","内容（３）"]
[null,1,null,null,null,1,1,1,null,{"$f":"$C11*$D11*$E11*$F11*$G11*$H11","v":0},{"$f":"$N11*O11","v":2000},null,1,100,20]
[null,2,null,null,null,1,1,1,null,{"$f":"$C12*$D12*$E12*$F12*$G12*$H12","v":0},{"$f":"$N12*O12","v":0},null,2]
[null,3,null,null,null,1,1,1,null,0,0,null,3]
[null,4,null,null,null,1,1,1,null,0,0,null,4]
[null,5,null,null,null,1,1,1,null,0,0,null,5]
[null,6,null,null,null,1,1,1,null,0,0,null,6]
[null,7,null,null,null,1,1,1,null,0,0,null,7]
[null,8,null,null,null,1,1,1,null,0,0,null,8]
[null,9,null,null,null,1,1,1,null,0,0,null,9]
[null,10,null,null,null,1,1,1,null,0,0,null,10]
[]
[null,"【浸透トレンチ】","単位設計浸透能（ｍ3/ｈｒ/m）",null,"設置数量\n（ｍ）","影響係数",null,null,null,null,null,null,"【浸透トレンチ】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,"（1）","（2）","（3）"]
[null,null,null,null,null,"内容（１）","内容（２）","内容（３）"]
[null,1,null,null,null,1,1,1,null,{"$f":"$C25*$D25*$E25*$F25*$G25*$H25","v":0},{"$f":"$N25*O25","v":0},null,1]
[null,2,null,null,null,1,1,1,null,{"$f":"$C26*$D26*$E26*$F26*$G26*$H26","v":0},0,null,2]
[null,3,null,null,null,1,1,1,null,0,0,null,3]
[null,4,null,null,null,1,1,1,null,0,0,null,4]
[null,5,null,null,null,1,1,1,null,0,0,null,5]
[null,6,null,null,null,1,1,1,null,0,0,null,6]
[null,7,null,null,null,1,1,1,null,0,0,null,7]
[null,8,null,null,null,1,1,1,null,0,0,null,8]
[null,9,null,null,null,1,1,1,null,0,0,null,9]
[null,10,null,null,null,1,1,1,null,0,0,null,10]
[]
[null,"【透水性舗装】","単位設計浸透能（ｍ3/ｈｒ/㎡）",null,"設置数量\n（㎡）","影響係数",null,null,null,null,null,null,"【透水性塗装】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,"（1）","（2）","（3）"]
[null,null,null,null,null,"内容（１）","内容（２）","内容（３）"]
[null,1,null,null,null,1,1,1,null,{"$f":"$C39*$D39*$E39*$F39*$G39*$H39","v":0},{"$f":"$N39*O39","v":0},null,1]
[null,2,null,null,null,1,1,1,null,{"$f":"$C40*$D40*$E40*$F40*$G40*$H40","v":0},{"$f":"$N40*O40","v":0},null,2]
[null,3,null,null,null,1,1,1,null,0,0,null,3]
[null,4,null,null,null,1,1,1,null,0,0,null,4]
[null,5,null,null,null,1,1,1,null,0,0,null,5]
[null,6,null,null,null,1,1,1,null,0,0,null,6]
[null,7,null,null,null,1,1,1,null,0,0,null,7]
[null,8,null,null,null,1,1,1,null,0,0,null,8]
[null,9,null,null,null,1,1,1,null,0,0,null,9]
[null,10,null,null,null,1,1,1,null,0,0,null,10]
[]
[null,"【その他】","単位設計浸透能（ｍ3/ｈｒ/単位）",null,"設置数量\n（単位）","影響係数",null,null,null,null,null,null,"【その他】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,"（1）","（2）","（3）"]
[null,null,null,null,null,"内容（１）","内容（２）","内容（３）"]
[null,1,null,null,null,1,1,1,null,{"$f":"$C53*$D53*$E53*$F53*$G53*$H53","v":0},{"$f":"$N53*O53","v":0},null,1]
[null,2,null,null,null,1,1,1,null,0,0,null,2]
[null,3,null,null,null,1,1,1,null,0,0,null,3]
[null,4,null,null,null,1,1,1,null,0,0,null,4]
[null,5,null,null,null,1,1,1,null,0,0,null,5]
[null,6,null,null,null,1,1,1,null,0,0,null,6]
[null,7,null,null,null,1,1,1,null,0,0,null,7]
[null,8,null,null,null,1,1,1,null,0,0,null,8]
[null,9,null,null,null,1,1,1,null,0,0,null,9]
[null,10,null,null,null,1,1,1,null,0,0,null,10]

{"sheet":"浸透施設能力（貯留浸透モデル_道路管理者用）","index":5,"n_rows":58,"n_cols":19,"rows_kept":58,"cut":false,"hidden":false,"merged":[[6,1,7,1],[6,6,6,7],[7,6,7,7],[1,7,1,8],[2,1,2,6],[4,1,4,2],[5,1,5,2],[5,6,5,7],[15,1,15,2],[15,9,15,10],[8,1,9,1],[8,6,8,7],[9,6,9,7],[10,1,10,6],[11,1,11,3],[12,1,12,2],[12,9,12,10],[13,1,13,2],[13,9,13,10],[14,1,14,2],[14,9,14,10],[16,1,16,2],[16,9,16,10],[17,1,17,2],[17,9,17,10],[18,1,18,2],[18,9,18,10],[27,1,27,2],[28,1,28,2],[21,1,21,6],[23,1,25,2],[23,3,23,4],[23,5,25,5],[23,6,25,6],[26,1,26,2],[23,18,25,18],[24,3,25,3],[24,4,25,4],[24,7,25,7],[24,8,25,8],[23,16,25,16],[23,17,25,17],[23,10,25,10],[23,11,25,11],[23,12,25,12],[23,15,25,15],[23,7,23,8],[29,1,29,2],[30,1,30,2],[31,1,31,2],[38,3,39,3],[38,4,39,4],[32,1,32,2],[33,1,33,2],[34,1,34,2],[35,1,35,2],[37,1,39,2],[37,3,37,4],[37,10,39,10],[37,11,39,11],[37,12,39,12],[52,6,52,7],[40,1,40,2],[41,1,41,2],[42,1,42,2],[43,1,43,2],[44,1,44,2],[45,1,45,2],[38,7,39,7],[38,8,39,8],[37,5,39,5],[37,6,39,6],[37,7,37,8],[53,1,53,2],[54,1,54,2],[46,1,46,2],[47,1,47,2],[48,1,48,2],[49,1,49,2],[52,1,52,2]]}
[]
["透水性舗装",null,null,null,null,null,null,"部分を入力して下さい"]
[]
[null,"基本諸元"]
[null,"設置数量(舗装面積) (m2)",null,3000]
[null,"飽和透水係数 （m/hr）",null,7.1999999999999998E-3,null,null,"上層路盤での貯留率(%)",null,{"$f":"L17","v":12.5}]
[null,"比浸透量算定定数\nK=aH+b","a",1.4E-2,null,null,"下層路盤での貯留率(%)",null,{"$f":"L18","v":4.5}]
[null,null,"b",1.2869999999999999,null,null,"下層路盤厚(mm)",null,{"$f":"D18","v":400}]
[null,"目詰まり\n係数","C1",0.9,null,null,"下層路盤での貯留量(mm)",null,{"$f":"M18","v":18}]
[null,null,"C2",0.9,null,null,"貯留量の合計(mm)",null,{"$f":"M19","v":55.5}]
[]
[null,"貯留率と水拘束率"]
[null,null,null,"厚さ(mm)","空気間隙率\n(%)","空気間隙率との関係","水拘束率\n(%)","水拘束量\n(mm)","貯留率\n(%)","貯留量\n(mm)",null,"STEP2での\n貯留率\n(%)","STEP2での\n貯留量\n(mm)"]
[null,"関係式",null,"a","b","b'","c","a×c/100","d (=b+b')","a×d/100",null,"d-c","a×(d-c)/100"]
[null,"表層",null,50,20,-6,1.5,{"$f":"D15*G15/100","v":0.75},{"$f":"E15+F15","v":14},{"$f":"D15*I15/100","v":7},null,{"$f":"I15-G15","v":12.5},{"$f":"D15*(I15-G15)/100","v":6.25}]
[null,"中間層・基層",null,100,20,-6,1.5,{"$f":"D16*G16/100","v":1.5},{"$f":"E16+F16","v":14},{"$f":"D16*I16/100","v":14},null,{"$f":"I16-G16","v":12.5},{"$f":"D16*(I16-G16)/100","v":12.5}]
[null,"上層路盤",null,150,20,-6,1.5,{"$f":"D17*G17/100","v":2.25},{"$f":"E17+F17","v":14},{"$f":"D17*I17/100","v":21},null,{"$f":"I17-G17","v":12.5},{"$f":"D17*(I17-G17)/100","v":18.75}]
[null,"下層路盤",null,400,8,-3,0.5,{"$f":"D18*G18/100","v":2},{"$f":"E18+F18","v":5},{"$f":"D18*I18/100","v":20},null,{"$f":"I18-G18","v":4.5},{"$f":"D18*(I18-G18)/100","v":18}]
[null,"合計",null,{"$f":"SUM(D15:D18)","v":700},"-","-","-",{"$f":"SUM(H15:H18)","v":6.5},"-",{"$f":"SUM(J15:J18)","v":62},null,"-",{"$f":"SUM(M15:M18)","v":55.5}]
[]
["浸透マス・トレンチ"]
[]
[null,"浸透能諸元",null,null,null,null,null,null,null,null,"空隙貯留諸元"]
[null,"【浸透マス】",null,"単位設計浸透能（ｍ3/ｈｒ/個）",null,"設置数量\n（個）","設計水頭\n(m)","影響係数",null,null,"【浸透\nマス】","体積\n（ｍ3）","空隙率\n（％）",null,null,"Σ","設計浸透量","平均設計水頭","設計空隙貯留量"]
[null,null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,null,"地下水位\n係数","目詰まり\n係数"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"小計"]
[null,1,null,10,7.1999999999999998E-3,10,0.8,1,1,null,1,500,20,null,null,{"$f":"D27*E27*F27*G27*H27*I27","v":0.57599999999999996},{"$f":"D27*E27*F27*H27*I27","v":0.72},null,{"$f":"L27*M27/100","v":100}]
[null,2,null,null,null,null,null,1,1,null,2,null,null,null,null,{"$f":"D28*E28*F28*G28*H28*I28","v":0},{"$f":"D28*E28*F28*H28*I28","v":0},null,{"$f":"L28*M28/100","v":0}]
[null,3,null,null,null,null,null,1,1,null,3,null,null,null,null,0,0,null,0]
[null,4,null,null,null,null,null,1,1,null,4,null,null,null,null,0,0,null,0]
[null,5,null,null,null,null,null,1,1,null,5,null,null,null,null,0,0,null,0]
[null,6,null,null,null,null,null,1,1,null,6,null,null,null,null,0,0,null,0]
[null,7,null,null,null,null,null,1,1,null,7,null,null,null,null,0,0,null,0]
[null,8,null,null,null,null,null,1,1,null,8,null,null,null,null,0,0,null,0]
[null,9,null,null,null,null,null,1,1,null,9,null,null,null,null,0,0,null,0]
[null,10,null,null,null,null,null,1,1,null,10,null,null,null,null,0,0,null,0]
[]
[null,"【浸透トレンチ】",null,"単位設計浸透能（ｍ3/ｈｒ/m）",null,"設置数量\n（ｍ）","設計水頭\n(m)","影響係数",null,null,"【浸透\nトレンチ】","体積\n（ｍ3）","空隙率\n（％）"]
[null,null,null,"比浸透量（㎡）","飽和透水係数\n（m/hr）",null,null,"地下水位\n係数","目詰まり\n係数"]
[]
[null,1,null,null,null,null,null,1,1,null,1,null,null,null,null,{"$f":"D41*E41*F41*G41*H41*I41","v":0},{"$f":"D41*E41*F41*H41*I41","v":0},null,{"$f":"L41*M41/100","v":0}]
[null,2,null,null,null,null,null,1,1,null,2,null,null,null,null,{"$f":"D42*E42*F42*G42*H42*I42","v":0},{"$f":"D42*E42*F42*H42*I42","v":0},null,0]
[null,3,null,null,null,null,null,1,1,null,3,null,null,null,null,0,0,null,0]
[null,4,null,null,null,null,null,1,1,null,4,null,null,null,null,0,0,null,0]
[null,5,null,null,null,null,null,1,1,null,5,null,null,null,null,0,0,null,0]
[null,6,null,null,null,null,null,1,1,null,6,null,null,null,null,0,0,null,0]
[null,7,null,null,null,null,null,1,1,null,7,null,null,null,null,0,0,null,0]
[null,8,null,null,null,null,null,1,1,null,8,null,null,null,null,0,0,null,0]
[null,9,null,null,null,null,null,1,1,null,9,null,null,null,null,0,0,null,0]
[null,10,null,null,null,null,null,1,1,null,10,null,null,null,null,0,0,null,0]
[]
[null,"統合諸元"]
[null,"設計浸透能(m3/hr)",null,{"$f":"Q55","v":0.72}]
[null,"平均設計水頭(m)",null,{"$f":"IF(D53>0,+R55,0)","v":0.79999999999999993}]
[null,"設計空隙貯留量(m3)",null,{"$f":"S55","v":100},null,null,null,null,null,null,null,null,null,null,"総合計",{"$f":"P57+P58","v":0.57599999999999996},{"$f":"Q57+Q58","v":0.72},{"$f":"P55/Q55","v":0.79999999999999993},{"$f":"S57+S58","v":100}]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"マス",{"$f":"SUM(P27:P36)","v":0.57599999999999996},{"$f":"SUM(Q27:Q36)","v":0.72},{"$f":"P57/Q57","v":0.79999999999999993},{"$f":"SUM(S27:S36)","v":100}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"トレンチ",{"$f":"SUM(P41:P50)","v":0},{"$f":"SUM(Q41:Q50)","v":0},{"$f":"P58/Q58","v":{"$error":"#DIV/0!"}},{"$f":"SUM(S41:S50)","v":0}]

{"sheet":"02流出計算（QT-Sグラフ）","index":6,"n_rows":149,"n_cols":10,"rows_kept":149,"cut":false,"hidden":false,"merged":[[7,2,8,5],[12,2,14,5],[1,1,1,5],[1,7,1,23]]}
[]
[null,"流 出 計 算 条 件",null,null,null,null,null,"流 出 計 算 結 果"]
[]
[null,null,null,null,null,null,null,"時刻","浸透考慮前","浸透考慮後"]
[null,1,"浸透施設なし",null,null,null,null,"00:00:00",0,0]
[null,null,null,null,null,null,null,"00:10:00",2.3500000000000001E-3,2.3500000000000001E-3]
[null,null,"浸透施設あり",null,null,null,null,"00:20:00",2.3800000000000002E-3,2.3800000000000002E-3]
[null,null,"※「浸透施設能力」シートに浸透施設諸元を入力してください。",null,null,null,null,"00:30:00",2.4099999999999998E-3,2.4099999999999998E-3]
[null,null,null,null,null,null,null,"00:40:00",2.4299999999999999E-3,2.4299999999999999E-3]
[null,null,null,null,null,null,null,"00:50:00",2.4599999999999999E-3,2.4599999999999999E-3]
[null,null,"浸透施設あり",null,null,null,null,"01:00:00",2.49E-3,2.49E-3]
[null,null,"（貯留浸透モデル_道路管理者用）",null,null,null,null,"01:10:00",2.5300000000000001E-3,2.5300000000000001E-3]
[null,null,"※「浸透施設能力（貯留浸透モデル_道路管理者用）」シートに浸透施設諸元を入力してください。",null,null,null,null,"01:20:00",2.5600000000000002E-3,2.5600000000000002E-3]
[null,null,null,null,null,null,null,"01:30:00",2.5899999999999999E-3,2.5899999999999999E-3]
[null,null,null,null,null,null,null,"01:40:00",2.63E-3,2.63E-3]
[null,null,null,null,null,null,null,"01:50:00",2.66E-3,2.66E-3]
[null,null,null,null,null,null,null,"02:00:00",2.7000000000000001E-3,2.7000000000000001E-3]
[null,null,null,null,null,null,null,"02:10:00",2.7399999999999998E-3,2.7399999999999998E-3]
[null,null,null,null,null,null,null,"02:20:00",2.7799999999999999E-3,2.7799999999999999E-3]
[null,null,null,null,null,null,null,"02:30:00",2.82E-3,2.82E-3]
[null,null,null,null,null,null,null,"02:40:00",2.8600000000000001E-3,2.8600000000000001E-3]
[null,null,null,null,null,null,null,"02:50:00",2.8999999999999998E-3,2.8999999999999998E-3]
[null,null,null,null,null,null,null,"03:00:00",2.9399999999999999E-3,2.9399999999999999E-3]
[null,null,null,null,null,null,null,"03:10:00",2.99E-3,2.99E-3]
[null,null,null,null,null,null,null,"03:20:00",3.0400000000000002E-3,3.0400000000000002E-3]
[null,null,null,null,null,null,null,"03:30:00",3.0899999999999999E-3,3.0899999999999999E-3]
[null,null,null,null,null,null,null,"03:40:00",3.14E-3,3.14E-3]
[null,null,null,null,null,null,null,"03:50:00",3.1900000000000001E-3,3.1900000000000001E-3]
[null,null,null,null,null,null,null,"04:00:00",3.2499999999999999E-3,3.2499999999999999E-3]
[null,null,null,null,null,null,null,"04:10:00",3.3E-3,3.3E-3]
[null,null,null,null,null,null,null,"04:20:00",3.3600000000000001E-3,3.3600000000000001E-3]
[null,null,null,null,null,null,null,"04:30:00",3.4299999999999999E-3,3.4299999999999999E-3]
[null,null,null,null,null,null,null,"04:40:00",3.49E-3,3.49E-3]
[null,null,null,null,null,null,null,"04:50:00",3.5599999999999998E-3,3.5599999999999998E-3]
[null,null,null,null,null,null,null,"05:00:00",3.63E-3,3.63E-3]
[null,null,null,null,null,null,null,"05:10:00",3.7000000000000002E-3,3.7000000000000002E-3]
[null,null,null,null,null,null,null,"05:20:00",3.7799999999999999E-3,3.7799999999999999E-3]
[null,null,null,null,null,null,null,"05:30:00",3.8600000000000001E-3,3.8600000000000001E-3]
[null,null,null,null,null,null,null,"05:40:00",3.9399999999999999E-3,3.9399999999999999E-3]
[null,null,null,null,null,null,null,"05:50:00",4.0299999999999997E-3,4.0299999999999997E-3]
[null,null,null,null,null,null,null,"06:00:00",4.13E-3,4.13E-3]
[null,null,null,null,null,null,null,"06:10:00",4.2199999999999998E-3,4.2199999999999998E-3]
[null,null,null,null,null,null,null,"06:20:00",4.3299999999999996E-3,4.3299999999999996E-3]
[null,null,null,null,null,null,null,"06:30:00",4.4400000000000004E-3,4.4400000000000004E-3]
[null,null,null,null,null,null,null,"06:40:00",4.5500000000000002E-3,4.5500000000000002E-3]
[null,null,null,null,null,null,null,"06:50:00",4.6699999999999997E-3,4.6699999999999997E-3]
[null,null,null,null,null,null,null,"07:00:00",4.7999999999999996E-3,4.7999999999999996E-3]
[null,null,null,null,null,null,null,"07:10:00",4.9399999999999999E-3,4.9399999999999999E-3]
[null,null,null,null,null,null,null,"07:20:00",5.0899999999999999E-3,5.0899999999999999E-3]
[null,null,null,null,null,null,null,"07:30:00",5.2399999999999999E-3,5.2399999999999999E-3]
[null,null,null,null,null,null,null,"07:40:00",5.4099999999999999E-3,5.4099999999999999E-3]
[null,null,null,null,null,null,null,"07:50:00",5.5900000000000004E-3,5.5900000000000004E-3]
[null,null,null,null,null,null,null,"08:00:00",5.7800000000000004E-3,5.7800000000000004E-3]
[null,null,null,null,null,null,null,"08:10:00",5.9899999999999997E-3,5.9899999999999997E-3]
[null,null,null,null,null,null,null,"08:20:00",6.2199999999999998E-3,6.2199999999999998E-3]
[null,null,null,null,null,null,null,"08:30:00",6.4599999999999996E-3,6.4599999999999996E-3]
[null,null,null,null,null,null,null,"08:40:00",6.7299999999999999E-3,6.7299999999999999E-3]
[null,null,null,null,null,null,null,"08:50:00",7.0200000000000002E-3,7.0200000000000002E-3]
[null,null,null,null,null,null,null,"09:00:00",7.3400000000000002E-3,7.3400000000000002E-3]
[null,null,null,null,null,null,null,"09:10:00",7.7000000000000002E-3,7.7000000000000002E-3]
[null,null,null,null,null,null,null,"09:20:00",8.09E-3,8.09E-3]
[null,null,null,null,null,null,null,"09:30:00",8.5299999999999994E-3,8.5299999999999994E-3]
[null,null,null,null,null,null,null,"09:40:00",9.0200000000000002E-3,9.0200000000000002E-3]
[null,null,null,null,null,null,null,"09:50:00",9.58E-3,9.58E-3]
[null,null,null,null,null,null,null,"10:00:00",1.022E-2,1.022E-2]
[null,null,null,null,null,null,null,"10:10:00",1.0959999999999999E-2,1.0959999999999999E-2]
[null,null,null,null,null,null,null,"10:20:00",1.1809999999999999E-2,1.1809999999999999E-2]
[null,null,null,null,null,null,null,"10:30:00",1.2829999999999999E-2,1.2829999999999999E-2]
[null,null,null,null,null,null,null,"10:40:00",1.6719999999999999E-2,1.6719999999999999E-2]
[null,null,null,null,null,null,null,"10:50:00",1.7809999999999999E-2,1.7809999999999999E-2]
[null,null,null,null,null,null,null,"11:00:00",1.915E-2,1.915E-2]
[null,null,null,null,null,null,null,"11:10:00",2.0840000000000001E-2,2.0840000000000001E-2]
[null,null,null,null,null,null,null,"11:20:00",2.3099999999999999E-2,2.3099999999999999E-2]
[null,null,null,null,null,null,null,"11:30:00",2.631E-2,2.631E-2]
[null,null,null,null,null,null,null,"11:40:00",3.143E-2,3.143E-2]
[null,null,null,null,null,null,null,"11:50:00",4.1739999999999999E-2,4.1739999999999999E-2]
[null,null,null,null,null,null,null,"12:00:00",0.10477,0.10477]
[null,null,null,null,null,null,null,"12:10:00",5.3499999999999999E-2,5.3499999999999999E-2]
[null,null,null,null,null,null,null,"12:20:00",3.5490000000000001E-2,3.5490000000000001E-2]
[null,null,null,null,null,null,null,"12:30:00",2.852E-2,2.852E-2]
[null,null,null,null,null,null,null,"12:40:00",2.4539999999999999E-2,2.4539999999999999E-2]
[null,null,null,null,null,null,null,"12:50:00",2.188E-2,2.188E-2]
[null,null,null,null,null,null,null,"13:00:00",1.9939999999999999E-2,1.9939999999999999E-2]
[null,null,null,null,null,null,null,"13:10:00",1.8440000000000002E-2,1.8440000000000002E-2]
[null,null,null,null,null,null,null,"13:20:00",1.7239999999999998E-2,1.7239999999999998E-2]
[null,null,null,null,null,null,null,"13:30:00",1.6250000000000001E-2,1.6250000000000001E-2]
[null,null,null,null,null,null,null,"13:40:00",1.23E-2,1.23E-2]
[null,null,null,null,null,null,null,"13:50:00",1.137E-2,1.137E-2]
[null,null,null,null,null,null,null,"14:00:00",1.057E-2,1.057E-2]
[null,null,null,null,null,null,null,"14:10:00",9.8899999999999995E-3,9.8899999999999995E-3]
[null,null,null,null,null,null,null,"14:20:00",9.2899999999999996E-3,9.2899999999999996E-3]
[null,null,null,null,null,null,null,"14:30:00",8.77E-3,8.77E-3]
[null,null,null,null,null,null,null,"14:40:00",8.3000000000000001E-3,8.3000000000000001E-3]
[null,null,null,null,null,null,null,"14:50:00",7.8899999999999994E-3,7.8899999999999994E-3]
[null,null,null,null,null,null,null,"15:00:00",7.5100000000000002E-3,7.5100000000000002E-3]
[null,null,null,null,null,null,null,"15:10:00",7.1799999999999998E-3,7.1799999999999998E-3]
[null,null,null,null,null,null,null,"15:20:00",6.8700000000000002E-3,6.8700000000000002E-3]
[null,null,null,null,null,null,null,"15:30:00",6.5900000000000004E-3,6.5900000000000004E-3]
[null,null,null,null,null,null,null,"15:40:00",6.3400000000000001E-3,6.3400000000000001E-3]
[null,null,null,null,null,null,null,"15:50:00",6.1000000000000004E-3,6.1000000000000004E-3]
[null,null,null,null,null,null,null,"16:00:00",5.8900000000000003E-3,5.8900000000000003E-3]
[null,null,null,null,null,null,null,"16:10:00",5.6899999999999997E-3,5.6899999999999997E-3]
[null,null,null,null,null,null,null,"16:20:00",5.4999999999999997E-3,5.4999999999999997E-3]
[null,null,null,null,null,null,null,"16:30:00",5.3299999999999997E-3,5.3299999999999997E-3]
[null,null,null,null,null,null,null,"16:40:00",5.1599999999999997E-3,5.1599999999999997E-3]
[null,null,null,null,null,null,null,"16:50:00",5.0099999999999997E-3,5.0099999999999997E-3]
[null,null,null,null,null,null,null,"17:00:00",4.8700000000000002E-3,4.8700000000000002E-3]
[null,null,null,null,null,null,null,"17:10:00",4.7400000000000003E-3,4.7400000000000003E-3]
[null,null,null,null,null,null,null,"17:20:00",4.6100000000000004E-3,4.6100000000000004E-3]
[null,null,null,null,null,null,null,"17:30:00",4.4900000000000001E-3,4.4900000000000001E-3]
[null,null,null,null,null,null,null,"17:40:00",4.3800000000000002E-3,4.3800000000000002E-3]
[null,null,null,null,null,null,null,"17:50:00",4.2700000000000004E-3,4.2700000000000004E-3]
[null,null,null,null,null,null,null,"18:00:00",4.1700000000000001E-3,4.1700000000000001E-3]
[null,null,null,null,null,null,null,"18:10:00",4.0800000000000003E-3,4.0800000000000003E-3]
[null,null,null,null,null,null,null,"18:20:00",3.9899999999999996E-3,3.9899999999999996E-3]
[null,null,null,null,null,null,null,"18:30:00",3.8999999999999998E-3,3.8999999999999998E-3]
[null,null,null,null,null,null,null,"18:40:00",3.82E-3,3.82E-3]
[null,null,null,null,null,null,null,"18:50:00",3.7399999999999998E-3,3.7399999999999998E-3]
[null,null,null,null,null,null,null,"19:00:00",3.6600000000000001E-3,3.6600000000000001E-3]
[null,null,null,null,null,null,null,"19:10:00",3.5899999999999999E-3,3.5899999999999999E-3]
[null,null,null,null,null,null,null,"19:20:00",3.5200000000000001E-3,3.5200000000000001E-3]
[null,null,null,null,null,null,null,"19:30:00",3.46E-3,3.46E-3]
[null,null,null,null,null,null,null,"19:40:00",3.3899999999999998E-3,3.3899999999999998E-3]
[null,null,null,null,null,null,null,"19:50:00",3.3300000000000001E-3,3.3300000000000001E-3]
[null,null,null,null,null,null,null,"20:00:00",3.2799999999999999E-3,3.2799999999999999E-3]
[null,null,null,null,null,null,null,"20:10:00",3.2200000000000002E-3,3.2200000000000002E-3]
[null,null,null,null,null,null,null,"20:20:00",3.16E-3,3.16E-3]
[null,null,null,null,null,null,null,"20:30:00",3.1099999999999999E-3,3.1099999999999999E-3]
[null,null,null,null,null,null,null,"20:40:00",3.0599999999999998E-3,3.0599999999999998E-3]
[null,null,null,null,null,null,null,"20:50:00",3.0100000000000001E-3,3.0100000000000001E-3]
[null,null,null,null,null,null,null,"21:00:00",2.97E-3,2.97E-3]
[null,null,null,null,null,null,null,"21:10:00",2.9199999999999999E-3,2.9199999999999999E-3]
[null,null,null,null,null,null,null,"21:20:00",2.8800000000000002E-3,2.8800000000000002E-3]
[null,null,null,null,null,null,null,"21:30:00",2.8400000000000001E-3,2.8400000000000001E-3]
[null,null,null,null,null,null,null,"21:40:00",2.8E-3,2.8E-3]
[null,null,null,null,null,null,null,"21:50:00",2.7599999999999999E-3,2.7599999999999999E-3]
[null,null,null,null,null,null,null,"22:00:00",2.7200000000000002E-3,2.7200000000000002E-3]
[null,null,null,null,null,null,null,"22:10:00",2.6800000000000001E-3,2.6800000000000001E-3]
[null,null,null,null,null,null,null,"22:20:00",2.64E-3,2.64E-3]
[null,null,null,null,null,null,null,"22:30:00",2.6099999999999999E-3,2.6099999999999999E-3]
[null,null,null,null,null,null,null,"22:40:00",2.5799999999999998E-3,2.5799999999999998E-3]
[null,null,null,null,null,null,null,"22:50:00",2.5400000000000002E-3,2.5400000000000002E-3]
[null,null,null,null,null,null,null,"23:00:00",2.5100000000000001E-3,2.5100000000000001E-3]
[null,null,null,null,null,null,null,"23:10:00",2.48E-3,2.48E-3]
[null,null,null,null,null,null,null,"23:20:00",2.4499999999999999E-3,2.4499999999999999E-3]
[null,null,null,null,null,null,null,"23:30:00",2.4199999999999998E-3,2.4199999999999998E-3]
[null,null,null,null,null,null,null,"23:40:00",2.3900000000000002E-3,2.3900000000000002E-3]
[null,null,null,null,null,null,null,"23:50:00",2.3600000000000001E-3,2.3600000000000001E-3]
[null,null,null,null,null,null,null,1,2.3400000000000001E-3,2.3400000000000001E-3]

{"sheet":"03-①調整池容量の概算","index":7,"n_rows":14,"n_cols":12,"rows_kept":14,"cut":false,"hidden":false,"merged":[[13,3,13,5],[8,8,8,11],[2,1,2,5],[4,4,5,4],[4,5,5,5],[8,4,9,4],[8,5,9,5]]}
["※①自然調節方式により調整地容量を概算する場合に入力してください"]
[]
[null,"入　力　条　件"]
[]
[null,null,"行為後ピーク流入量",null,{"$f":"MAX('02流出計算（QT-Sグラフ）'!$J$5:$J$149)","v":0.10477},"m3/s"]
[null,null,"（浸透考慮後）"]
[]
[null,"調整池諸元"]
[null,null,"許容放流量",null,{"$f":"MAX('01流出計算（Q-Tグラフ）'!$I$5:$I$149)","v":3.4729999999999997E-2},"m3/s",null,null,"概　算　結　果"]
[null,null,"（行為前ピーク流入量）"]
[null,null,null,null,null,null,null,null,null,"必要容量",700,"m3/ha"]
[null,null,"調整池高",null,1,"m"]
[]
[null,"浸透施設条件",null,{"$f":"IF('02流出計算（QT-Sグラフ）'!$B$5=1,\"浸透施設なし\",IF('02流出計算（QT-Sグラフ）'!$B$5=2,\"浸透施設あり\",\"浸透施設あり（貯留浸透モデル_道路管理者用）\"))","v":"浸透施設なし"},null,null,{"$f":"'02流出計算（QT-Sグラフ）'!$B$5","v":1},null,null,"オリフィス径（円管、直径）",0.114,"m"]

{"sheet":"04-①調節計算（自然調節方式）","index":8,"n_rows":151,"n_cols":26,"rows_kept":151,"cut":false,"hidden":false,"merged":[[3,20,3,25],[24,15,24,16],[3,1,3,8],[5,12,6,12],[5,13,6,13],[8,12,9,12],[8,13,9,13],[3,10,3,13],[13,15,13,16],[10,15,11,18],[28,15,29,18],[31,15,31,18],[1,1,1,13],[15,15,15,16],[17,15,17,16],[20,15,20,16],[22,15,22,16]]}
[]
[null,"入　力　条　件"]
[]
[null,"設 定 調 整 池 諸 元",null,null,null,null,null,null,null,null,"行 為 後 流 入 量",null,null,null,null,null,null,null,null,null,"計　算　結　果　（時　系　列）"]
[]
[null,"水深-容量",null,null,null,null,"放流口形状",null,null,null,"行為後ピーク流入量",null,{"$f":"MAX('02流出計算（QT-Sグラフ）'!$J$5:$J$149)","v":0.10477},"m3/s",null,null,null,null,null,null,"時刻","行為後流入量","浸透考慮後流入量","許容放流量","調節後放流量","調整池水位"]
[null,"No","水深H（m）","容量V（m3）",null,null,"（口径）",null,null,null,"（浸透考慮後）",null,null,null,null,null,null,null,null,null,"00:00:00",0,0,3.4729999999999997E-2,0,0]
[null,1,0,0,null,1,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"00:10:00",2.3500000000000001E-3,2.3500000000000001E-3,3.4729999999999997E-2,4.4717179580093148E-6,1.4073169692251945E-3]
[null,2,1,500,null,null,"直径",0.05,"m",null,"許容放流量",null,{"$f":"MAX('01流出計算（Q-Tグラフ）'!$I$5:$I$149)","v":3.4729999999999997E-2},"m3/s",null,null,null,null,null,null,"00:20:00",2.3800000000000002E-3,2.3800000000000002E-3,3.4729999999999997E-2,2.1326564977719907E-5,4.2298379994637567E-3]
[null,3,null,null,null,null,null,null,null,null,"（行為前ピーク流入量）",null,null,null,null,null,null,null,null,null,"00:30:00",2.4099999999999998E-3,2.4099999999999998E-3,3.4729999999999997E-2,4.7516508906239202E-5,7.0625321551333817E-3]
[null,4,null,null,null,null,null,null,null,null,null,null,null,null,null,"計　算　結　果",null,null,null,null,"00:40:00",2.4299999999999999E-3,2.4299999999999999E-3,3.4729999999999997E-2,7.8420582341451615E-5,9.8909699003847679E-3]
[null,5,null,null,null,null,"高さ",0.3,"m",null,null,null,null,null,null,null,null,null,null,null,"00:50:00",2.4599999999999999E-3,2.4599999999999999E-3,3.4729999999999997E-2,1.1409130392631728E-4,1.2709462768624107E-2]
[null,6,null,null,null,null,"幅",0.09,"m",null,null,null,null,null,null,null,null,null,null,null,"01:00:00",2.49E-3,2.49E-3,3.4729999999999997E-2,1.5396007575304443E-4,1.551863194081649E-2]
[null,7,null,null,null,null,null,null,null,null,null,null,null,null,null,"総合評価",null,"O.K",null,null,"01:10:00",2.5300000000000001E-3,2.5300000000000001E-3,3.4729999999999997E-2,1.9762388072887797E-4,1.8319681566927336E-2]
[null,8,null,null,null,null,"（管底位置）",null,null,null,null,null,null,null,null,null,null,null,null,null,"01:20:00",2.5600000000000002E-3,2.5600000000000002E-3,3.4729999999999997E-2,2.4477760962499177E-4,2.1108240672715013E-2]
[null,9,null,null,null,null,"池底高から",0,"m",null,null,null,null,null,null,"放流量評価",null,"許容放流量以下",null,null,"01:30:00",2.5899999999999999E-3,2.5899999999999999E-3,3.4729999999999997E-2,2.9292365988572668E-4,2.3875619911008582E-2]
[null,10,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"01:40:00",2.63E-3,2.63E-3,3.4729999999999997E-2,3.4624800125697587E-4,2.6624116914322961E-2]
[null,11,null,null,null,null,null,null,null,null,null,null,null,null,null,"池の容量不足",null,"無",null,null,"01:50:00",2.66E-3,2.66E-3,3.4729999999999997E-2,3.9996261321261509E-4,2.9350390545641206E-2]
[null,12,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:00:00",2.7000000000000001E-3,2.7000000000000001E-3,3.4729999999999997E-2,4.5619914989471092E-4,3.2052693487776812E-2]
[null,13,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:10:00",2.7399999999999998E-3,2.7399999999999998E-3,3.4729999999999997E-2,5.1484920295992778E-4,3.4734064476064037E-2]
[null,14,null,null,null,null,null,null,null,null,null,null,null,null,null,"最大放流量",null,4.8597752474278805E-3,"m3/s",null,"02:20:00",2.7799999999999999E-3,2.7799999999999999E-3,3.4729999999999997E-2,5.758172543984376E-4,3.7391664601649013E-2]
[null,15,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:30:00",2.82E-3,2.82E-3,3.4729999999999997E-2,6.3901830694569801E-4,4.0022763264842533E-2]
[null,16,null,null,null,null,null,null,null,null,null,null,null,null,null,"池内最大水深",null,0.8931829259021461,"m",null,"02:40:00",2.8600000000000001E-3,2.8600000000000001E-3,3.4729999999999997E-2,7.0437608311078404E-4,4.2624726630808643E-2]
[null,17,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:50:00",2.8999999999999998E-3,2.8999999999999998E-3,3.4729999999999997E-2,7.6560563412999335E-4,4.5198737600464174E-2]
[null,18,null,null,null,null,null,null,null,null,null,null,null,null,null,"池内最大ボリューム",null,446.59146295107303,"m3",null,"03:00:00",2.9399999999999999E-3,2.9399999999999999E-3,3.4729999999999997E-2,8.3170185624138933E-4,4.7744353106241345E-2]
[null,19,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:10:00",2.99E-3,2.99E-3,3.4729999999999997E-2,8.9632449992385881E-4,5.0265537292542198E-2]
[null,20,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:20:00",3.0400000000000002E-3,3.0400000000000002E-3,3.4729999999999997E-2,9.692468075001916E-4,5.2764194508087767E-2]
[null,21,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:30:00",3.0899999999999999E-3,3.0899999999999999E-3,3.4729999999999997E-2,1.037169740461513E-3,5.5238344579310747E-2]
[null,22,null,null,null,null,null,null,null,null,null,null,null,null,null,"許 可 申 請 図 書 の 作 成",null,null,null,null,"03:40:00",3.14E-3,3.14E-3,3.4729999999999997E-2,1.1066091217769324E-3,5.7690077261967683E-2]
[null,23,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:50:00",3.1900000000000001E-3,3.1900000000000001E-3,3.4729999999999997E-2,1.1731825384504843E-3,6.012020226583123E-2]
[null,24,null,null,null,null,null,null,null,null,null,null,null,null,null,"■【様式】許可申請図書の保存場所",null,null,null,null,"04:00:00",3.2499999999999999E-3,3.2499999999999999E-3,3.4729999999999997E-2,1.18600018799225E-3,6.2568692629965589E-2]
[null,25,null,null,null,null,null,null,null,null,null,null,null,null,null,"C:\\71期",null,null,null,null,"04:10:00",3.3E-3,3.3E-3,3.4729999999999997E-2,1.1988178375340157E-3,6.5067801814649828E-2]
[null,26,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:20:00",3.3600000000000001E-3,3.3600000000000001E-3,3.4729999999999997E-2,1.2122763695528698E-3,6.7617145290397696E-2]
[null,27,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:30:00",3.4299999999999999E-3,3.4299999999999999E-3,3.4729999999999997E-2,1.226375784048812E-3,7.0227953998236683E-2]
[null,28,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:40:00",3.49E-3,3.49E-3,3.4729999999999997E-2,1.2404751985447544E-3,7.289984340868054E-2]
[null,29,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:50:00",3.5599999999999998E-3,3.5599999999999998E-3,3.4729999999999997E-2,1.2545746130406966E-3,7.5632813521729278E-2]
[null,30,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:00:00",3.63E-3,3.63E-3,3.4729999999999997E-2,1.268674027536639E-3,7.8432864337382877E-2]
[null,31,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:10:00",3.7000000000000002E-3,3.7000000000000002E-3,3.4729999999999997E-2,1.2840552069867577E-3,8.1299226796668844E-2]
[null,32,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:20:00",3.7799999999999999E-3,3.7799999999999999E-3,3.4729999999999997E-2,1.2994363864368766E-3,8.4237131840614668E-2]
[null,33,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:30:00",3.8600000000000001E-3,3.8600000000000001E-3,3.4729999999999997E-2,1.3148175658869955E-3,8.725257946922034E-2]
[null,34,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:40:00",3.9399999999999999E-3,3.9399999999999999E-3,3.4729999999999997E-2,1.3331292479826472E-3,9.0343811380898559E-2]
[null,35,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:50:00",4.0299999999999997E-3,4.0299999999999997E-3,3.4729999999999997E-2,1.3651269342396968E-3,9.3506857671565163E-2]
[null,36,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:00:00",4.13E-3,4.13E-3,3.4729999999999997E-2,1.3963916002850236E-3,9.6745946550850323E-2]
[null,37,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:10:00",4.2199999999999998E-3,4.2199999999999998E-3,3.4729999999999997E-2,1.4292966232527949E-3,0.10006053361672762]
[null,38,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:20:00",4.3299999999999996E-3,4.3299999999999996E-3,3.4729999999999997E-2,1.4614609721566682E-3,0.10345607905948195]
[null,39,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:30:00",4.4400000000000004E-3,4.4400000000000004E-3,3.4729999999999997E-2,1.4929325199192316E-3,0.1069454429642364]
[null,40,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:40:00",4.5500000000000002E-3,4.5500000000000002E-3,3.4729999999999997E-2,1.5259319205203866E-3,0.11052812429997264]
[null,41,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:50:00",4.6699999999999997E-3,4.6699999999999997E-3,3.4729999999999997E-2,1.5582326344592082E-3,0.11420962556698487]
[null,42,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:00:00",4.7999999999999996E-3,4.7999999999999996E-3,3.4729999999999997E-2,1.5898772468729569E-3,0.11800275963818557]
[null,43,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:10:00",4.9399999999999999E-3,4.9399999999999999E-3,3.4729999999999997E-2,1.6229515575920184E-3,0.12191906235550658]
[null,44,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:20:00",5.0899999999999999E-3,5.0899999999999999E-3,3.4729999999999997E-2,1.6573699760740693E-3,0.12596886943530694]
[null,45,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:30:00",5.2399999999999999E-3,5.2399999999999999E-3,3.4729999999999997E-2,1.6910880275411929E-3,0.13015779463313776]
[null,46,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:40:00",5.4099999999999999E-3,5.4099999999999999E-3,3.4729999999999997E-2,1.7260717184781002E-3,0.13449749878552619]
[null,47,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:50:00",5.5900000000000004E-3,5.5900000000000004E-3,3.4729999999999997E-2,1.760360314755681E-3,0.13900563956558593]
[null,48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:00:00",5.7800000000000004E-3,5.7800000000000004E-3,3.4729999999999997E-2,1.7967680345293781E-3,0.14369336255601489]
[null,49,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:10:00",5.9899999999999997E-3,5.9899999999999997E-3,3.4729999999999997E-2,1.8333583917538043E-3,0.148577286700245]
[null,50,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:20:00",6.2199999999999998E-3,6.2199999999999998E-3,3.4729999999999997E-2,1.8710082833747702E-3,0.15368066669516783]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:30:00",6.4599999999999996E-3,6.4599999999999996E-3,3.4729999999999997E-2,1.9096550425234632E-3,0.1590202686996289]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:40:00",6.7299999999999999E-3,6.7299999999999999E-3,3.4729999999999997E-2,1.949239376666948E-3,0.16461893204811465]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:50:00",7.0200000000000002E-3,7.0200000000000002E-3,3.4729999999999997E-2,1.9897053286348685E-3,0.17050556522493357]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:00:00",7.3400000000000002E-3,7.3400000000000002E-3,3.4729999999999997E-2,2.0310002026544469E-3,0.17670914190615999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:10:00",7.7000000000000002E-3,7.7000000000000002E-3,3.4729999999999997E-2,2.074675664733544E-3,0.18326973638572722]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:20:00",8.09E-3,8.09E-3,3.4729999999999997E-2,2.120584628531362E-3,0.19022658020976826]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:30:00",8.5299999999999994E-3,8.5299999999999994E-3,3.4729999999999997E-2,2.1670534374640584E-3,0.197625997370171]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:40:00",9.0200000000000002E-3,9.0200000000000002E-3,3.4729999999999997E-2,2.2155461622716966E-3,0.20552643761032957]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:50:00",9.58E-3,9.58E-3,3.4729999999999997E-2,2.2673978779418104E-3,0.21399667118620147]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:00:00",1.022E-2,1.022E-2,3.4729999999999997E-2,2.3216685658102982E-3,0.22312323131995021]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:10:00",1.0959999999999999E-2,1.0959999999999999E-2,3.4729999999999997E-2,2.3788906795929902E-3,0.23301089577270823]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:20:00",1.1809999999999999E-2,1.1809999999999999E-2,3.4729999999999997E-2,2.4395371764765069E-3,0.24378183905906653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:30:00",1.2829999999999999E-2,1.2829999999999999E-2,3.4729999999999997E-2,2.5046853336251115E-3,0.25559930555300558]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:40:00",1.6719999999999999E-2,1.6719999999999999E-2,3.4729999999999997E-2,2.5830082246480228E-3,0.27027668941804167]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:50:00",1.7809999999999999E-2,1.7809999999999999E-2,3.4729999999999997E-2,2.6739691341424354E-3,0.28784050300276737]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:00:00",1.915E-2,1.915E-2,3.4729999999999997E-2,2.7685407651573657E-3,0.30675099706318748]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:10:00",2.0840000000000001E-2,2.0840000000000001E-2,3.4729999999999997E-2,2.8675240162394046E-3,0.32736335819434942]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:20:00",2.3099999999999999E-2,2.3099999999999999E-2,3.4729999999999997E-2,2.9743879724130084E-3,0.35022221100115797]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:30:00",2.631E-2,2.631E-2,3.4729999999999997E-2,3.0910016016418968E-3,0.37622897725672505]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:40:00",3.143E-2,3.143E-2,3.4729999999999997E-2,3.2240387117678832E-3,0.40708395306867917]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:50:00",4.1739999999999999E-2,4.1739999999999999E-2,3.4729999999999997E-2,3.3882578754593023E-3,0.44701857511634291]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:00:00",0.10477,0.10477,3.4729999999999997E-2,3.7092162460614451E-3,0.53066609064343051]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:10:00",5.3499999999999999E-2,5.3499999999999999E-2,3.4729999999999997E-2,4.0264470056822817E-3,0.62098669269238427]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:20:00",3.5490000000000001E-2,3.5490000000000001E-2,3.4729999999999997E-2,4.1869546982192286E-3,0.66945265167004331]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:30:00",2.852E-2,2.852E-2,3.4729999999999997E-2,4.2938488759991277E-3,0.7027701695255123]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:40:00",2.4539999999999999E-2,2.4539999999999999E-2,3.4729999999999997E-2,4.3773335163858626E-3,0.72940346009008139]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:50:00",2.188E-2,2.188E-2,3.4729999999999997E-2,4.4469513679258237E-3,0.75196088915949444]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:00:00",1.9939999999999999E-2,1.9939999999999999E-2,3.4729999999999997E-2,4.5070309895387742E-3,0.77168049974501562]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:10:00",1.8440000000000002E-2,1.8440000000000002E-2,3.4729999999999997E-2,4.559770584405533E-3,0.78926841880064902]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:20:00",1.7239999999999998E-2,1.7239999999999998E-2,3.4729999999999997E-2,4.6068641781812341E-3,0.80517643794309701]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:30:00",1.6250000000000001E-2,1.6250000000000001E-2,3.4729999999999997E-2,4.6495547887689592E-3,0.8197165865629269]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:40:00",1.23E-2,1.23E-2,3.4729999999999997E-2,4.6833562044430012E-3,0.83124683996699966]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:50:00",1.137E-2,1.137E-2,3.4729999999999997E-2,4.7081072287526475E-3,0.83981396190708235]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:00:00",1.057E-2,1.057E-2,3.4729999999999997E-2,4.729921404487563E-3,0.8473151447271382]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:10:00",9.8899999999999995E-3,9.8899999999999995E-3,3.4729999999999997E-2,4.7484895590826663E-3,0.85390409814899604]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:20:00",9.2899999999999996E-3,9.2899999999999996E-3,3.4729999999999997E-2,4.7648951247009031E-3,0.85970406733872584]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:30:00",8.77E-3,8.77E-3,3.4729999999999997E-2,4.7795077731123473E-3,0.86481342560003793]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:40:00",8.3000000000000001E-3,8.3000000000000001E-3,3.4729999999999997E-2,4.7926903503996065E-3,0.86931210672593084]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:50:00",7.8899999999999994E-3,7.8899999999999994E-3,3.4729999999999997E-2,4.803763409346835E-3,0.87326823447008295]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:00:00",7.5100000000000002E-3,7.5100000000000002E-3,3.4729999999999997E-2,4.8134314401344488E-3,0.87673791756039421]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:10:00",7.1799999999999998E-3,7.1799999999999998E-3,3.4729999999999997E-2,4.8220472304890388E-3,0.87977063035802006]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:20:00",6.8700000000000002E-3,6.8700000000000002E-3,3.4729999999999997E-2,4.8292726155176264E-3,0.88240983845041598]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:30:00",6.5900000000000004E-3,6.5900000000000004E-3,3.4729999999999997E-2,4.8361438984321197E-3,0.88468658854204618]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:40:00",6.3400000000000001E-3,6.3400000000000001E-3,3.4729999999999997E-2,4.841633903490147E-3,0.88663792186089274]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:50:00",6.1000000000000004E-3,6.1000000000000004E-3,3.4729999999999997E-2,4.8460899530245191E-3,0.888289287546984]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:00:00",5.8900000000000003E-3,5.8900000000000003E-3,3.4729999999999997E-2,4.8498572586262532E-3,0.8896657192199936]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:10:00",5.6899999999999997E-3,5.6899999999999997E-3,3.4729999999999997E-2,4.8532795442593913E-3,0.89079183713826215]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:20:00",5.4999999999999997E-3,5.4999999999999997E-3,3.4729999999999997E-2,4.8553317577826509E-3,0.89168067035703691]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:30:00",5.3299999999999997E-3,5.3299999999999997E-3,3.4729999999999997E-2,4.8573831042588054E-3,0.89235104143981203]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:40:00",5.1599999999999997E-3,5.1599999999999997E-3,3.4729999999999997E-2,4.8587501874257392E-3,0.89281536146480134]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:50:00",5.0099999999999997E-3,5.0099999999999997E-3,3.4729999999999997E-2,4.8594335847858879E-3,0.89308645120147434]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:00:00",4.8700000000000002E-3,4.8700000000000002E-3,3.4729999999999997E-2,4.8597752474278805E-3,0.8931829259021461]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:10:00",4.7400000000000003E-3,4.7400000000000003E-3,3.4729999999999997E-2,4.8597752474278805E-3,0.89311719560523262]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:20:00",4.6100000000000004E-3,4.6100000000000004E-3,3.4729999999999997E-2,4.8590918981201974E-3,0.89289587531790382]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:30:00",4.4900000000000001E-3,4.4900000000000001E-3,3.4729999999999997E-2,4.8577249111190516E-3,0.89252578523236026]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:40:00",4.3800000000000002E-3,4.3800000000000002E-3,3.4729999999999997E-2,4.8563575393329346E-3,0.89201933576208914]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:50:00",4.2700000000000004E-3,4.2700000000000004E-3,3.4729999999999997E-2,4.8549897824367331E-3,0.89138252736902734]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:00:00",4.1700000000000001E-3,4.1700000000000001E-3,3.4729999999999997E-2,4.8525952802177174E-3,0.89062197633143469]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:10:00",4.0800000000000003E-3,4.0800000000000003E-3,3.4729999999999997E-2,4.8501995958534988E-3,0.88975029940579187]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:20:00",3.9899999999999996E-3,3.9899999999999996E-3,3.4729999999999997E-2,4.8474602210926846E-3,0.88877370351562424]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:30:00",3.8999999999999998E-3,3.8999999999999998E-3,3.4729999999999997E-2,4.844376572890133E-3,0.88769260143923456]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:40:00",3.82E-3,3.82E-3,3.4729999999999997E-2,4.8409479933469498E-3,0.8865134066994923]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:50:00",3.7399999999999998E-3,3.7399999999999998E-3,3.4729999999999997E-2,4.8375169838061529E-3,0.88524232771320044]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:00:00",3.6600000000000001E-3,3.6600000000000001E-3,3.4729999999999997E-2,4.8333965574739179E-3,0.88387977958843233]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:10:00",3.5899999999999999E-3,3.5899999999999999E-3,3.4729999999999997E-2,4.8296164118443357E-3,0.88243197180684141]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:20:00",3.5200000000000001E-3,3.5200000000000001E-3,3.4729999999999997E-2,4.8254892393149E-3,0.88090490841614588]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:30:00",3.46E-3,3.46E-3,3.4729999999999997E-2,4.8206697388222166E-3,0.87930521302926368]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:40:00",3.3899999999999998E-3,3.3899999999999998E-3,3.4729999999999997E-2,4.8158454151736039E-3,0.87763330393686612]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:50:00",3.3300000000000001E-3,3.3300000000000001E-3,3.4729999999999997E-2,4.8110162538595718E-3,0.87588918693544626]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:00:00",3.2799999999999999E-3,3.2799999999999999E-3,3.4729999999999997E-2,4.806182240297734E-3,0.87408486783895178]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:10:00",3.2200000000000002E-3,3.2200000000000002E-3,3.4729999999999997E-2,4.8006516930381793E-3,0.87222076747895028]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:20:00",3.16E-3,3.16E-3,3.4729999999999997E-2,4.7951147670089516E-3,0.87029130760292195]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:30:00",3.1099999999999999E-3,3.1099999999999999E-3,3.4729999999999997E-2,4.7895714400877564E-3,0.86830249587866404]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:40:00",3.0599999999999998E-3,3.0599999999999998E-3,3.4729999999999997E-2,4.7840216900241258E-3,0.86626034000059693]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:50:00",3.0100000000000001E-3,3.0100000000000001E-3,3.4729999999999997E-2,4.7777705156697202E-3,0.86416526467718058]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:00:00",2.97E-3,2.97E-3,3.4729999999999997E-2,4.7715111516357699E-3,0.86202369567679737]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:10:00",2.9199999999999999E-3,2.9199999999999999E-3,3.4729999999999997E-2,4.7652435656497273E-3,0.85983564284642611]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:20:00",2.8800000000000002E-3,2.8800000000000002E-3,3.4729999999999997E-2,4.7589677252265258E-3,0.85760111607190037]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:30:00",2.8400000000000001E-3,2.8400000000000001E-3,3.4729999999999997E-2,4.7526835976666225E-3,0.85532612527816443]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:40:00",2.8E-3,2.8E-3,3.4729999999999997E-2,4.7460413250142762E-3,0.8530108903245559]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:50:00",2.7599999999999999E-3,2.7599999999999999E-3,3.4729999999999997E-2,4.7390394013333021E-3,0.85065584188874743]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:00:00",2.7200000000000002E-3,2.7200000000000002E-3,3.4729999999999997E-2,4.7323779779940896E-3,0.84826099146115097]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:10:00",2.6800000000000001E-3,2.6800000000000001E-3,3.4729999999999997E-2,4.7253558083227617E-3,0.84582635118936078]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:20:00",2.64E-3,2.64E-3,3.4729999999999997E-2,4.7183231877326818E-3,0.84335214379172763]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:30:00",2.6099999999999999E-3,2.6099999999999999E-3,3.4729999999999997E-2,4.7112800694229726E-3,0.84084438183743415]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:40:00",2.5799999999999998E-3,2.5799999999999998E-3,3.4729999999999997E-2,4.7035204581305891E-3,0.838309501520902]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:50:00",2.5400000000000002E-3,2.5400000000000002E-3,3.4729999999999997E-2,4.6964551407097689E-3,0.83574151616159786]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:00:00",2.5100000000000001E-3,2.5100000000000001E-3,3.4729999999999997E-2,4.6886709946647011E-3,0.83314044048037317]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:10:00",2.48E-3,2.48E-3,3.4729999999999997E-2,4.6808739038475423E-3,0.83051271354126588]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:20:00",2.4499999999999999E-3,2.4499999999999999E-3,3.4729999999999997E-2,4.6730638034625412E-3,0.82785835091687976]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:30:00",2.4199999999999998E-3,2.4199999999999998E-3,3.4729999999999997E-2,4.6655965116274619E-3,0.82517715472782571]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:40:00",2.3900000000000002E-3,2.3900000000000002E-3,3.4729999999999997E-2,4.6577607942895902E-3,0.82246914034427554]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:50:00",2.3600000000000001E-3,2.3600000000000001E-3,3.4729999999999997E-2,4.6499118727489934E-3,0.81973453674405228]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2.3400000000000001E-3,2.3400000000000001E-3,3.4729999999999997E-2,4.6413342748295493E-3,0.81697978905550517]

{"sheet":"04-②調節計算（2段）","index":9,"n_rows":151,"n_cols":26,"rows_kept":151,"cut":false,"hidden":false,"merged":[[14,10,15,11],[14,12,15,12],[14,13,15,13],[15,15,15,16],[8,10,9,11],[8,12,9,12],[8,13,9,13],[11,10,12,11],[11,12,12,12],[11,13,12,13],[13,15,13,16],[10,15,11,18],[1,1,1,13],[3,1,3,8],[3,10,3,13],[5,12,6,12],[5,13,6,13],[28,15,29,18],[31,15,31,18],[3,20,3,25],[26,15,26,16],[17,15,17,16],[20,15,20,16],[22,15,22,16],[24,15,24,16]]}
[]
[null,"入　力　条　件"]
[]
[null,"設 定 調 整 池 諸 元",null,null,null,null,null,null,null,null,"行 為 後 流 入 量",null,null,null,null,null,null,null,null,null,"計　算　結　果　（時　系　列）"]
[]
[null,"水深-容量",null,null,null,null,"■上段オリフィス",null,null,null,"行為後ピーク流入量",null,{"$f":"MAX('02流出計算（QT-Sグラフ）'!$J$5:$J$149)","v":0.10477},"m3/s",null,null,null,null,null,null,"時刻","行為後流入量","浸透考慮後流入量","許容放流量","調節後放流量","調整池水位"]
[null,"No","水深H（m）","容量V（m3）",null,null,"放流口形状",null,null,null,"（浸透考慮後）",null,null,null,null,null,null,null,null,null,"00:00:00",0,0,1.933E-2,0,0]
[null,1,0,0,null,1,"（口径）",null,null,null,null,null,null,null,null,null,null,null,null,null,"00:10:00",2.0999999999999999E-3,0,1.933E-2,0,0]
[null,2,3,300,null,null,null,null,null,null,"許容放流量（計）",null,{"$f":"MAX('01流出計算（Q-Tグラフ）'!$I$5:$I$149)","v":3.4729999999999997E-2},"m3/s",null,null,null,null,null,null,"00:20:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,3,null,null,null,null,"直径",0.1,"m",null,null,null,null,null,null,null,null,null,null,null,"00:30:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,4,null,null,null,null,null,null,null,null,null,null,null,null,null,"計　算　結　果",null,null,null,null,"00:40:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,5,null,null,null,null,null,null,null,null,"許容放流量（上段）",null,null,"m3/s",null,null,null,null,null,null,"00:50:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,6,null,null,null,null,"高さ",null,"m",null,null,null,null,null,null,null,null,null,null,null,"01:00:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,7,null,null,null,null,"幅",null,"m",null,null,null,null,null,null,"総合評価",null,"O.K",null,null,"01:10:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,8,null,null,null,null,null,null,null,null,"許容放流量（下段）",null,{"$f":"M9-M12","v":3.4729999999999997E-2},"m3/s",null,null,null,null,null,null,"01:20:00",2.33E-3,0,1.933E-2,0,0]
[null,9,null,null,null,null,"（管底位置）",null,null,null,null,null,null,null,null,"放流量評価",null,"許容放流量以下",null,null,"01:30:00",2.33E-3,0,1.933E-2,0,0]
[null,10,null,null,null,null,"池底高から",1,"m",null,null,null,null,null,null,null,null,null,null,null,"01:40:00",2.33E-3,0,1.933E-2,0,0]
[null,11,null,null,null,null,null,null,null,null,null,null,null,null,null,"池の容量不足",null,"無",null,null,"01:50:00",2.3999999999999998E-3,0,1.933E-2,0,0]
[null,12,null,null,null,null,"■下段オリフィス",null,null,null,null,null,null,null,null,null,null,null,null,null,"02:00:00",2.3999999999999998E-3,0,1.933E-2,0,0]
[null,13,null,null,null,null,"放流口形状",null,null,null,null,null,null,null,null,null,null,null,null,null,"02:10:00",2.47E-3,0,1.933E-2,0,0]
[null,14,null,null,null,null,"（口径）",null,null,null,null,null,null,null,null,"最大放流量（上段+下段）",null,2.4454520287668694E-3,"m3/s",null,"02:20:00",2.47E-3,0,1.933E-2,0,0]
[null,15,null,null,null,2,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:30:00",2.47E-3,0,1.933E-2,0,0]
[null,16,null,null,null,null,"直径",null,"m",null,null,null,null,null,null,"最大放流量（下段）",null,2.4454520287668694E-3,"m3/s",null,"02:40:00",2.5500000000000002E-3,0,1.933E-2,0,0]
[null,17,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:50:00",2.5500000000000002E-3,0,1.933E-2,0,0]
[null,18,null,null,null,null,null,null,null,null,null,null,null,null,null,"池内最大水深",null,0.85246185640973493,"m",null,"03:00:00",2.6199999999999999E-3,0,1.933E-2,0,0]
[null,19,null,null,null,null,"高さ",0.01,"m",null,null,null,null,null,null,null,null,null,null,null,"03:10:00",2.6199999999999999E-3,0,1.933E-2,0,0]
[null,20,null,null,null,null,"幅",0.1,"m",null,null,null,null,null,null,"池内最大ボリューム",null,85.246185640973493,"m3",null,"03:20:00",2.7000000000000001E-3,0,1.933E-2,0,0]
[null,21,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:30:00",2.7000000000000001E-3,0,1.933E-2,0,0]
[null,22,null,null,null,null,"（管底位置）",null,null,null,null,null,null,null,null,"許 可 申 請 図 書 の 作 成",null,null,null,null,"03:40:00",2.7799999999999999E-3,0,1.933E-2,0,0]
[null,23,null,null,null,null,"池底高から",0,"m",null,null,null,null,null,null,null,null,null,null,null,"03:50:00",2.7799999999999999E-3,0,1.933E-2,0,0]
[null,24,null,null,null,null,null,null,null,null,null,null,null,null,null,"■申請図書様式の保存場所",null,null,null,null,"04:00:00",2.8500000000000001E-3,0,1.933E-2,0,0]
[null,25,null,null,null,null,null,null,null,null,null,null,null,null,null,"C:\\【様式】許可申請図書.xls",null,null,null,null,"04:10:00",2.9199999999999999E-3,0,1.933E-2,0,0]
[null,26,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:20:00",2.9199999999999999E-3,0,1.933E-2,0,0]
[null,27,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:30:00",3.0000000000000001E-3,0,1.933E-2,0,0]
[null,28,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:40:00",3.0000000000000001E-3,0,1.933E-2,0,0]
[null,29,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:50:00",3.0799999999999998E-3,0,1.933E-2,0,0]
[null,30,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:00:00",3.15E-3,0,1.933E-2,0,0]
[null,31,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:10:00",3.2200000000000002E-3,0,1.933E-2,0,0]
[null,32,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:20:00",3.2200000000000002E-3,0,1.933E-2,0,0]
[null,33,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:30:00",3.3E-3,0,1.933E-2,0,0]
[null,34,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:40:00",3.3700000000000002E-3,0,1.933E-2,0,0]
[null,35,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:50:00",3.4499999999999999E-3,0,1.933E-2,0,0]
[null,36,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:00:00",3.5300000000000002E-3,0,1.933E-2,0,0]
[null,37,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:10:00",3.5999999999999999E-3,0,1.933E-2,0,0]
[null,38,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:20:00",3.6800000000000001E-3,0,1.933E-2,0,0]
[null,39,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:30:00",3.7499999999999999E-3,0,1.933E-2,0,0]
[null,40,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:40:00",3.82E-3,0,1.933E-2,0,0]
[null,41,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:50:00",3.8999999999999998E-3,0,1.933E-2,0,0]
[null,42,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:00:00",4.0499999999999998E-3,0,1.933E-2,0,0]
[null,43,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:10:00",4.1200000000000004E-3,0,1.933E-2,0,0]
[null,44,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:20:00",4.1999999999999997E-3,0,1.933E-2,0,0]
[null,45,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:30:00",4.3499999999999997E-3,0,1.933E-2,0,0]
[null,46,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:40:00",4.4999999999999997E-3,0,1.933E-2,0,0]
[null,47,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:50:00",4.5799999999999999E-3,0,1.933E-2,0,0]
[null,48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:00:00",4.7200000000000002E-3,0,1.933E-2,0,0]
[null,49,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:10:00",4.8799999999999998E-3,0,1.933E-2,0,0]
[null,50,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:20:00",5.0299999999999997E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:30:00",5.2500000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:40:00",5.4000000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:50:00",5.62E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:00:00",5.8500000000000002E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:10:00",6.1500000000000001E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:20:00",6.3800000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:30:00",6.7499999999999999E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:40:00",7.0499999999999998E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:50:00",7.4200000000000004E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:00:00",7.9500000000000005E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:10:00",8.3999999999999995E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:20:00",9.0799999999999995E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:30:00",9.75E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:40:00",1.065E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:50:00",1.17E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:00:00",1.3050000000000001E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:10:00",1.485E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:20:00",1.7330000000000002E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:30:00",2.0920000000000001E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:40:00",2.6919999999999999E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:50:00",3.9149999999999997E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:00:00",8.6999999999999994E-2,3.0508715650547653E-2,1.933E-2,7.7066217976004244E-4,8.9214160412362825E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:10:00",5.2200000000000003E-2,4.5708999999999993E-2,1.933E-2,1.4696308130147857E-3,0.3111464283856813]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:20:00",3.1800000000000002E-2,2.5304000000000004E-2,1.933E-2,1.8954245072014869E-3,0.51409026242503242]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:30:00",2.3550000000000001E-2,1.7050999999999993E-2,1.933E-2,2.0985721708461683E-3,0.62917327239088949]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:40:00",1.8970000000000001E-2,1.2468999999999989E-2,1.933E-2,2.2220706401209437E-3,0.70477134395798813]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:50:00",1.5980000000000001E-2,9.4779999999999847E-3,1.933E-2,2.3034356303411217E-3,0.75703582514660184]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:00:00",1.388E-2,7.378E-3,1.933E-2,2.3588586521080487E-3,0.79361694229925428]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:10:00",1.2370000000000001E-2,5.8679999999999904E-3,1.933E-2,2.3966228436463465E-3,0.81908849781199111]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:20:00",1.1180000000000001E-2,4.6779999999999929E-3,1.933E-2,2.421827475340161E-3,0.83627114685503134]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:30:00",1.0200000000000001E-2,3.6980000000000029E-3,1.933E-2,2.4372492419093084E-3,0.84682191670328311]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:40:00",9.3799999999999994E-3,2.8779999999999956E-3,1.933E-2,2.4446594135865839E-3,0.85190419073679535]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:50:00",8.6999999999999994E-3,2.1979999999999934E-3,1.933E-2,2.4454520287668694E-3,0.85246185640973493]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:00:00",8.1799999999999998E-3,1.6779999999999972E-3,1.933E-2,2.4409571396918259E-3,0.84943062890435883]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:10:00",7.6499999999999997E-3,1.1480000000000008E-3,1.933E-2,2.4319424383478939E-3,0.84328993017023968]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:20:00",7.28E-3,7.7799999999998682E-4,1.933E-2,2.4194256323815783E-3,0.83451382595805113]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:30:00",6.8999999999999999E-3,3.9799999999999612E-4,1.933E-2,2.4033520048829717E-3,0.82357349304625738]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:40:00",6.5199999999999998E-3,1.7999999999981735E-5,1.933E-2,2.3839205989032016E-3,0.81045967523489881]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:50:00",6.2199999999999998E-3,0,1.933E-2,2.3629629754690403E-3,0.79627302451178195]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:00:00",6.0000000000000001E-3,0,1.933E-2,2.3418178035449298E-3,0.78215868217474016]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:10:00",5.7800000000000004E-3,0,1.933E-2,2.3204799560785907E-3,0.76817178889586957]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:20:00",5.5500000000000002E-3,0,1.933E-2,2.2995059931428747E-3,0.75431183104820521]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:30:00",5.3200000000000001E-3,0,1.933E-2,2.2783389560022669E-3,0.74057829620076976]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:40:00",5.1799999999999997E-3,0,1.933E-2,2.2569734124209349E-3,0.72697235909550018]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:50:00",4.9500000000000004E-3,0,1.933E-2,2.2359815640312195E-3,0.71349349416614383]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:00:00",4.7999999999999996E-3,0,1.933E-2,2.2147907632550754E-3,0.70014117718428481]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:10:00",4.6499999999999996E-3,0,1.933E-2,2.1936897427621803E-3,0.6869157356662331]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:20:00",4.4999999999999997E-3,0,1.933E-2,2.1723837713442805E-3,0.67381751512391364]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:30:00",4.4299999999999999E-3,0,1.933E-2,2.1511670796773314E-3,0.66084686257084879]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:40:00",4.2700000000000004E-3,0,1.933E-2,2.1300423356268063E-3,0.64800323432493634]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:50:00",4.1999999999999997E-3,0,1.933E-2,2.1090123021511751E-3,0.63528607041160245]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:00:00",4.0499999999999998E-3,0,1.933E-2,2.087770444681958E-3,0.62269572217110314]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:10:00",3.98E-3,0,1.933E-2,2.0666228395470471E-3,0.61023254231841606]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:20:00",3.8999999999999998E-3,0,1.933E-2,2.0452565834602511E-3,0.59789690404939411]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:30:00",3.82E-3,0,1.933E-2,2.0243030918843398E-3,0.58568822502336026]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:40:00",3.6800000000000001E-3,0,1.933E-2,2.0031304309598764E-3,0.57360592445482761]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:50:00",3.5999999999999999E-3,0,1.933E-2,1.9817315759361812E-3,0.5616513384341395]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:00:00",3.5300000000000002E-3,0,1.933E-2,1.9607581541491799E-3,0.54982386924388338]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:10:00",3.4499999999999999E-3,0,1.933E-2,1.9395579493952995E-3,0.53812292093324987]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:20:00",3.3700000000000002E-3,0,1.933E-2,1.9184601979843105E-3,0.52654886649111099]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:30:00",3.3700000000000002E-3,0,1.933E-2,1.8971278352914174E-3,0.51510210239128396]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:40:00",3.3E-3,0,1.933E-2,1.8758972540660376E-3,0.50378302712321144]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:50:00",3.2200000000000002E-3,0,1.933E-2,1.8547719494253195E-3,0.49259101951273737]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:00:00",3.15E-3,0,1.933E-2,1.8337555598075225E-3,0.48152543698503886]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:10:00",3.0799999999999998E-3,0,1.933E-2,1.8124954956840582E-3,0.47058668381856411]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:20:00",3.0799999999999998E-3,0,1.933E-2,1.7913437366436683E-3,0.45977516612158098]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:30:00",3.0000000000000001E-3,0,1.933E-2,1.7703041648082683E-3,0.44909022241722518]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:40:00",2.9199999999999999E-3,0,1.933E-2,1.7490115177043572E-3,0.43853227536968725]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:50:00",2.9199999999999999E-3,0,1.933E-2,1.7278303546283123E-3,0.42810174975268933]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:00:00",2.8500000000000001E-3,0,1.933E-2,1.7067648261769985E-3,0.41779796421027338]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:10:00",2.8500000000000001E-3,0,1.933E-2,1.6854360294520226E-3,0.4076213616433863]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:20:00",2.7799999999999999E-3,0,1.933E-2,1.6642220522101309E-3,0.39757238739839984]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:30:00",2.7799999999999999E-3,0,1.933E-2,1.6431273416681678E-3,0.38765033921676501]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:40:00",2.7000000000000001E-3,0,1.933E-2,1.6221565507064969E-3,0.37785448753964102]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:50:00",2.7000000000000001E-3,0,1.933E-2,1.6009110809356338E-3,0.36818528464471456]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:00:00",2.6199999999999999E-3,0,1.933E-2,1.579788813516699E-3,0.35864318496135761]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:10:00",2.6199999999999999E-3,0,1.933E-2,1.5583802814340599E-3,0.34922867767650528]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:20:00",2.5500000000000002E-3,0,1.933E-2,1.5370938487938852E-3,0.3399422552858215]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:30:00",2.5500000000000002E-3,0,1.933E-2,1.5159346590882469E-3,0.33078316976217509]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:40:00",2.47E-3,0,1.933E-2,1.4949081153828483E-3,0.32175064143876181]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:50:00",2.47E-3,0,1.933E-2,1.4740198941796882E-3,0.31284385741007414]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:00:00",2.3999999999999998E-3,0,1.933E-2,1.4528313816260646E-3,0.30406330358265693]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:10:00",2.3999999999999998E-3,0,1.933E-2,1.4313292418020043E-3,0.29541082171237271]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:20:00",2.3999999999999998E-3,0,1.933E-2,1.4104154557478799E-3,0.28688558761972305]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:30:00",2.33E-3,0,1.933E-2,1.3891868546698461E-3,0.27848678068846988]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:40:00",2.33E-3,0,1.933E-2,1.3681010447879937E-3,0.27021491699009642]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:50:00",2.33E-3,0,1.933E-2,1.346685122926848E-3,0.26207055848695188]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:00:00",2.2499999999999998E-3,0,1.933E-2,1.3258978679558996E-3,0.25405280951430359]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:10:00",2.2499999999999998E-3,0,1.933E-2,1.3042842864958543E-3,0.24616226305094832]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:20:00",2.2499999999999998E-3,0,1.933E-2,1.2833136125378706E-3,0.23839946935384718]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:30:00",2.1700000000000001E-3,0,1.933E-2,1.2619945151425976E-3,0.23076354497080578]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:40:00",2.1700000000000001E-3,0,1.933E-2,1.2408297532548532E-3,0.22325507216561344]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:50:00",2.1700000000000001E-3,0,1.933E-2,1.2198273603516603E-3,0.21587310082479386]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2.0999999999999999E-3,0,1.933E-2,1.1984569669214243E-3,0.20861824784297461]

{"sheet":"04-③調節計算（ポンプ）","index":10,"n_rows":151,"n_cols":26,"rows_kept":151,"cut":false,"hidden":false,"merged":[[11,9,12,10],[11,11,12,11],[11,12,12,12],[14,9,15,10],[1,1,1,12],[3,9,3,12],[5,11,6,11],[5,12,6,12],[8,11,9,11],[8,12,9,12],[3,1,3,3],[3,5,3,7],[31,15,31,18],[22,15,22,16],[28,15,29,18],[14,11,15,11],[3,20,3,25],[13,15,13,16],[15,15,15,16],[17,15,17,16],[14,12,15,12],[24,15,24,16],[10,15,11,18],[20,15,20,16]]}
[]
[null,"入　力　条　件"]
[]
[null,"設 定 調 整 池 諸 元",null,null,null,"放 流 ポ ン プ 諸 元",null,null,null,"行 為 後 流 入 量",null,null,null,null,null,null,null,null,null,null,"計　算　結　果　（時　系　列）"]
[]
[null,"水深-容量",null,null,null,"水深-ポンプ",null,null,null,"行為後ピーク流入量",null,{"$f":"MAX('02流出計算（QT-Sグラフ）'!$J$5:$J$149)","v":0.10477},"m3/s",null,null,null,null,null,null,null,"時刻","行為後流入量","浸透考慮後流入量","許容放流量","調節後放流量","調整池水位"]
[null,"No","水深H（m）","容量V（m3）",null,"No","水深H（m）","ポンプ規模Q(m3/s)",null,"（浸透考慮後）",null,null,null,null,null,null,null,null,null,null,"00:00:00",0,0,1.933E-2,0,0]
[null,1,0,0,null,1,0,0,null,null,null,null,null,null,null,null,null,null,null,null,"00:10:00",2.0999999999999999E-3,0,1.933E-2,0,0]
[null,2,3,90,null,2,3,1.4999999999999999E-2,null,"許容放流量",null,{"$f":"MAX('01流出計算（Q-Tグラフ）'!$I$5:$I$149)","v":3.4729999999999997E-2},"m3/s",null,null,null,null,null,null,null,"00:20:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,3,null,null,null,3,null,null,null,"（行為前ピーク流入量）",null,null,null,null,null,null,null,null,null,null,"00:30:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,4,null,null,null,4,null,null,null,null,null,null,null,null,null,"計　算　結　果",null,null,null,null,"00:40:00",2.1700000000000001E-3,0,1.933E-2,0,0]
[null,5,null,null,null,5,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"00:50:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,6,null,null,null,6,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"01:00:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,7,null,null,null,7,null,null,null,null,null,null,null,null,null,"総合評価",null,"O.K",null,null,"01:10:00",2.2499999999999998E-3,0,1.933E-2,0,0]
[null,8,null,null,null,8,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"01:20:00",2.33E-3,0,1.933E-2,0,0]
[null,9,null,null,null,9,null,null,null,null,null,null,null,null,null,"放流量評価",null,"許容放流量以下",null,null,"01:30:00",2.33E-3,0,1.933E-2,0,0]
[null,10,null,null,null,10,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"01:40:00",2.33E-3,0,1.933E-2,0,0]
[null,11,null,null,null,11,null,null,null,null,null,null,null,null,null,"池の容量不足",null,"無",null,null,"01:50:00",2.3999999999999998E-3,0,1.933E-2,0,0]
[null,12,null,null,null,12,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:00:00",2.3999999999999998E-3,0,1.933E-2,0,0]
[null,13,null,null,null,13,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:10:00",2.47E-3,0,1.933E-2,0,0]
[null,14,null,null,null,14,null,null,null,null,null,null,null,null,null,"最大放流量",null,9.7851562499999996E-3,"m3/s",null,"02:20:00",2.47E-3,0,1.933E-2,0,0]
[null,15,null,null,null,15,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:30:00",2.47E-3,0,1.933E-2,0,0]
[null,16,null,null,null,16,null,null,null,null,null,null,null,null,null,"池内最大水深",null,1.9570632876203276,"m",null,"02:40:00",2.5500000000000002E-3,0,1.933E-2,0,0]
[null,17,null,null,null,17,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"02:50:00",2.5500000000000002E-3,0,1.933E-2,0,0]
[null,18,null,null,null,18,null,null,null,null,null,null,null,null,null,"池内最大ボリューム",null,58.711898628609823,"m3",null,"03:00:00",2.6199999999999999E-3,0,1.933E-2,0,0]
[null,19,null,null,null,19,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:10:00",2.6199999999999999E-3,0,1.933E-2,0,0]
[null,20,null,null,null,20,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:20:00",2.7000000000000001E-3,0,1.933E-2,0,0]
[null,21,null,null,null,21,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:30:00",2.7000000000000001E-3,0,1.933E-2,0,0]
[null,22,null,null,null,22,null,null,null,null,null,null,null,null,null,"許 可 申 請 図 書 の 作 成",null,null,null,null,"03:40:00",2.7799999999999999E-3,0,1.933E-2,0,0]
[null,23,null,null,null,23,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"03:50:00",2.7799999999999999E-3,0,1.933E-2,0,0]
[null,24,null,null,null,24,null,null,null,null,null,null,null,null,null,"■申請図書様式の保存場所",null,null,null,null,"04:00:00",2.8500000000000001E-3,0,1.933E-2,0,0]
[null,25,null,null,null,25,null,null,null,null,null,null,null,null,null,"C:\\【様式】許可申請図書.xls",null,null,null,null,"04:10:00",2.9199999999999999E-3,0,1.933E-2,0,0]
[null,26,null,null,null,26,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:20:00",2.9199999999999999E-3,0,1.933E-2,0,0]
[null,27,null,null,null,27,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:30:00",3.0000000000000001E-3,0,1.933E-2,0,0]
[null,28,null,null,null,28,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:40:00",3.0000000000000001E-3,0,1.933E-2,0,0]
[null,29,null,null,null,29,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"04:50:00",3.0799999999999998E-3,0,1.933E-2,0,0]
[null,30,null,null,null,30,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:00:00",3.15E-3,0,1.933E-2,0,0]
[null,31,null,null,null,31,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:10:00",3.2200000000000002E-3,0,1.933E-2,0,0]
[null,32,null,null,null,32,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:20:00",3.2200000000000002E-3,0,1.933E-2,0,0]
[null,33,null,null,null,33,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:30:00",3.3E-3,0,1.933E-2,0,0]
[null,34,null,null,null,34,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:40:00",3.3700000000000002E-3,0,1.933E-2,0,0]
[null,35,null,null,null,35,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"05:50:00",3.4499999999999999E-3,0,1.933E-2,0,0]
[null,36,null,null,null,36,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:00:00",3.5300000000000002E-3,0,1.933E-2,0,0]
[null,37,null,null,null,37,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:10:00",3.5999999999999999E-3,0,1.933E-2,0,0]
[null,38,null,null,null,38,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:20:00",3.6800000000000001E-3,0,1.933E-2,0,0]
[null,39,null,null,null,39,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:30:00",3.7499999999999999E-3,0,1.933E-2,0,0]
[null,40,null,null,null,40,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:40:00",3.82E-3,0,1.933E-2,0,0]
[null,41,null,null,null,41,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"06:50:00",3.8999999999999998E-3,0,1.933E-2,0,0]
[null,42,null,null,null,42,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:00:00",4.0499999999999998E-3,0,1.933E-2,0,0]
[null,43,null,null,null,43,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:10:00",4.1200000000000004E-3,0,1.933E-2,0,0]
[null,44,null,null,null,44,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:20:00",4.1999999999999997E-3,0,1.933E-2,0,0]
[null,45,null,null,null,45,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:30:00",4.3499999999999997E-3,0,1.933E-2,0,0]
[null,46,null,null,null,46,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:40:00",4.4999999999999997E-3,0,1.933E-2,0,0]
[null,47,null,null,null,47,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"07:50:00",4.5799999999999999E-3,0,1.933E-2,0,0]
[null,48,null,null,null,48,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:00:00",4.7200000000000002E-3,0,1.933E-2,0,0]
[null,49,null,null,null,49,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:10:00",4.8799999999999998E-3,0,1.933E-2,0,0]
[null,50,null,null,null,50,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:20:00",5.0299999999999997E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:30:00",5.2500000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:40:00",5.4000000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"08:50:00",5.62E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:00:00",5.8500000000000002E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:10:00",6.1500000000000001E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:20:00",6.3800000000000003E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:30:00",6.7499999999999999E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:40:00",7.0499999999999998E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"09:50:00",7.4200000000000004E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:00:00",7.9500000000000005E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:10:00",8.3999999999999995E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:20:00",9.0799999999999995E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:30:00",9.75E-3,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:40:00",1.065E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10:50:00",1.17E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:00:00",1.3050000000000001E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:10:00",1.485E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:20:00",1.7330000000000002E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:30:00",2.0920000000000001E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:40:00",2.6919999999999999E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"11:50:00",3.9149999999999997E-2,0,1.933E-2,0,0]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:00:00",8.6999999999999994E-2,3.0508715650547653E-2,1.933E-2,1.4529418945312498E-3,0.29055773756016401]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:10:00",5.2200000000000003E-2,4.5708999999999993E-2,1.933E-2,4.94384765625E-3,0.98876699855782801]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:20:00",3.1800000000000002E-2,2.5304000000000004E-2,1.933E-2,7.8543090820312501E-3,1.5709154311750155]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:30:00",2.3550000000000001E-2,1.7050999999999993E-2,1.933E-2,9.1232299804687497E-3,1.8246900405500153]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:40:00",1.8970000000000001E-2,1.2468999999999989E-2,1.933E-2,9.6606445312500001E-3,1.9320512954328277]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"12:50:00",1.5980000000000001E-2,9.4779999999999847E-3,1.933E-2,9.7851562499999996E-3,1.9570632876203276]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:00:00",1.388E-2,7.378E-3,1.933E-2,9.6560668945312508E-3,1.9312110561750147]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:10:00",1.2370000000000001E-2,5.8679999999999904E-3,1.933E-2,9.3667602539062502E-3,1.8734427846906399]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:20:00",1.1180000000000001E-2,4.6779999999999929E-3,1.933E-2,8.9776611328125002E-3,1.7954585708234521]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:30:00",1.0200000000000001E-2,3.6980000000000029E-3,1.933E-2,8.5208129882812494E-3,1.7042338296125144]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:40:00",9.3799999999999994E-3,2.8779999999999956E-3,1.933E-2,8.0227661132812496E-3,1.6045580385968896]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"13:50:00",8.6999999999999994E-3,2.1979999999999934E-3,1.933E-2,7.4999999999999997E-3,1.5000903774640768]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:00:00",8.1799999999999998E-3,1.6779999999999972E-3,1.933E-2,6.9708251953124996E-3,1.3941421255109518]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:10:00",7.6499999999999997E-3,1.1480000000000008E-3,1.933E-2,6.4416503906250004E-3,1.2882773696515768]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:20:00",7.28E-3,7.7799999999998682E-4,1.933E-2,5.9197998046874997E-3,1.1839228676984517]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:30:00",6.8999999999999999E-3,3.9799999999999612E-4,1.933E-2,5.4116821289062504E-3,1.082368048362514]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:40:00",6.5199999999999998E-3,1.7999999999981735E-5,1.933E-2,4.9163818359374998E-3,0.98324740871407623]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"14:50:00",6.2199999999999998E-3,0,1.933E-2,4.4485473632812503E-3,0.88977811672188856]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:00:00",6.0000000000000001E-3,0,1.933E-2,4.0255737304687499E-3,0.80503690578438858]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:10:00",5.7800000000000004E-3,0,1.933E-2,3.6419677734374997E-3,0.72836149074532608]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:20:00",5.5500000000000002E-3,0,1.933E-2,3.2949829101562495E-3,0.65899198390938851]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:30:00",5.3200000000000001E-3,0,1.933E-2,2.9809570312499998E-3,0.59623258449532601]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:40:00",5.1799999999999997E-3,0,1.933E-2,2.6971435546874999E-3,0.53945157863595106]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"15:50:00",4.9500000000000004E-3,0,1.933E-2,2.4407958984375001E-3,0.48807218410470105]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:00:00",4.7999999999999996E-3,0,1.933E-2,2.208251953125E-3,0.44158170558907606]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:10:00",4.6499999999999996E-3,0,1.933E-2,1.9976806640624998E-3,0.39952237941720103]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:20:00",4.4999999999999997E-3,0,1.933E-2,1.8072509765625E-3,0.36147306301095106]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:30:00",4.4299999999999999E-3,0,1.933E-2,1.6351318359374997E-3,0.32704923488595106]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:40:00",4.2700000000000004E-3,0,1.933E-2,1.4794921874999999E-3,0.29590299465157605]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"16:50:00",4.1999999999999997E-3,0,1.933E-2,1.3385009765624998E-3,0.26772306301095106]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:00:00",4.0499999999999998E-3,0,1.933E-2,1.2112426757812499E-3,0.24222562648751353]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:10:00",3.98E-3,0,1.933E-2,1.0958862304687499E-3,0.21915433742501353]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:20:00",3.8999999999999998E-3,0,1.933E-2,9.9151611328125006E-4,0.19828031398751353]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:30:00",3.82E-3,0,1.933E-2,8.9721679687500007E-4,0.17939298488595104]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:40:00",3.6800000000000001E-3,0,1.933E-2,8.1115722656249995E-4,0.16230924465157603]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"17:50:00",3.5999999999999999E-3,0,1.933E-2,7.3425292968749996E-4,0.14685514308907605]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:00:00",3.5300000000000002E-3,0,1.933E-2,6.6467285156250003E-4,0.13286588527657603]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:10:00",3.4499999999999999E-3,0,1.933E-2,6.0058593749999999E-4,0.12021329738595105]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:20:00",3.3700000000000002E-3,0,1.933E-2,5.4382324218750001E-4,0.10876920558907605]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:30:00",3.3700000000000002E-3,0,1.933E-2,4.9163818359374998E-4,9.841459133126354E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:40:00",3.3E-3,0,1.933E-2,4.4494628906249995E-4,8.9048746604701037E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"18:50:00",3.2200000000000002E-3,0,1.933E-2,4.0283203125000003E-4,8.0570963401576046E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:00:00",3.15E-3,0,1.933E-2,3.6437988281249998E-4,7.2898844260951043E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:10:00",3.0799999999999998E-3,0,1.933E-2,3.2958984374999997E-4,6.595914699532604E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:20:00",3.0799999999999998E-3,0,1.933E-2,2.9846191406249998E-4,5.9678629417201041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:30:00",3.0000000000000001E-3,0,1.933E-2,2.7008056640624999E-4,5.3993204612513543E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:40:00",2.9199999999999999E-3,0,1.933E-2,2.4444580078124999E-4,4.8847940940638539E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"19:50:00",2.9199999999999999E-3,0,1.933E-2,2.2064208984374999E-4,4.4197062034388543E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:00:00",2.8500000000000001E-3,0,1.933E-2,1.995849609375E-4,3.9994791526576041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:10:00",2.8500000000000001E-3,0,1.933E-2,1.8127441406250001E-4,3.6186197776576043E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:20:00",2.7799999999999999E-3,0,1.933E-2,1.6387939453125E-4,3.2734659690638539E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:30:00",2.7799999999999999E-3,0,1.933E-2,1.4831542968750001E-4,2.9612711448451044E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:40:00",2.7000000000000001E-3,0,1.933E-2,1.336669921875E-4,2.6792887229701041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"20:50:00",2.7000000000000001E-3,0,1.933E-2,1.2084960937499999E-4,2.4247721214076041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:00:00",2.6199999999999999E-3,0,1.933E-2,1.0986328124999999E-4,2.1940592307826041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:10:00",2.6199999999999999E-3,0,1.933E-2,9.8876953124999993E-5,1.9853189964076041E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:20:00",2.5500000000000002E-3,0,1.933E-2,8.9721679687499998E-5,1.7967203635951043E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:30:00",2.5500000000000002E-3,0,1.933E-2,8.1481933593749998E-5,1.6255167503138542E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:40:00",2.47E-3,0,1.933E-2,7.3242187499999997E-5,1.4707926292201043E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"21:50:00",2.47E-3,0,1.933E-2,6.6833496093749998E-5,1.3307169456263541E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:00:00",2.3999999999999998E-3,0,1.933E-2,6.0424804687499993E-5,1.2034586448451042E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:10:00",2.3999999999999998E-3,0,1.933E-2,5.4016113281249994E-5,1.0890177268763542E-2]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:20:00",2.3999999999999998E-3,0,1.933E-2,4.9438476562499996E-5,9.8556313703260425E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:30:00",2.33E-3,0,1.933E-2,4.4860839843749999E-5,8.9126382062635415E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:40:00",2.33E-3,0,1.933E-2,4.0283203125000002E-5,8.0611977765760422E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"22:50:00",2.33E-3,0,1.933E-2,3.6621093749999999E-5,7.2921548078260416E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:00:00",2.2499999999999998E-3,0,1.933E-2,3.2958984374999995E-5,6.5963540265760422E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:10:00",2.2499999999999998E-3,0,1.933E-2,3.0212402343749996E-5,5.9646401593885416E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:20:00",2.2499999999999998E-3,0,1.933E-2,2.655029296875E-5,5.3970132062635418E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:30:00",2.1700000000000001E-3,0,1.933E-2,2.4719238281249998E-5,4.8843178937635423E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:40:00",2.1700000000000001E-3,0,1.933E-2,2.1972656250000003E-5,4.417398948451042E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"23:50:00",2.1700000000000001E-3,0,1.933E-2,2.0141601562500001E-5,3.9962563703260416E-3]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1,2.0999999999999999E-3,0,1.933E-2,1.8310546874999999E-5,3.6117348859510418E-3]